## Summary
SUMMARY OF PRICES (To be submitted with priced part of the offer)
COMPOSITE WORKS IN VARIOUS CNG STATIONS AT EAST & WEST GODAVARI DISTRICTS OF ANDHRA PRADESH
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
Sl. No. |  | Price Currency IN INR
|  | (In Figures) | (In Words)
1 | Total amount of quoted price for Daughter Booster Station
i) | Mechanical Works
ii) | Electrical Works
2 | Total amount of quoted price for District Regulatory Skid
i) | Civil Works
ii) | Electrical Works
iii) | Mechanical Works
iv) | Steel Structural Works
3 | Total amount of quoted price for CNG Works
i) | Civil Works
ii) | Electrical Works
iii) | Instrumentation works
iv) | Mechanical Works
v) | Steel Structural Works
vi) | Architectural Works
4 | Gross Total Amount (inclusive of all applicable taxes & duties excluding GST)
1 +2+3
5 | GST @ ____ net Total Amount mentioned at Sl. No. 4 above.
6 | Total Amount (Sl. No. 4 + 5)
Place | : |  | Signature of Authorised Signatory
Date | : |  | Name :
Designation :
Seal :
Tender No.:
Offer No. & Date :

## DBS Mech
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DAUGHTER BOOSTER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG online station with bus dispensers | Quantity for 1(one) no. of CNG Daughter Booster Station in RO | Total Quantity for 8 nos. CNG Daughter booster station | Unit Rate | Total Amount Exclusive of GST for 8 nos. of CNG stations
|  |  |  | A | B | C | D=C*B
PART - I : Mechanical & Piping Works
| SECTION-A : SS TUBE LAYING & TESTING | - | - |  | - |  | -
1.0 (a) | Laying with PVC heavy duty tube clamp of Swagelok/Parker/DK-Lok/Vaishnavi Hydraulics/Vardhaman bearings/AK Industries, Pneumatic testing with Nitrogen at 280 bar and commissioning of SS tubes along with fittings and valves as given below and as per Technical Specification and scope of work including handling, lifting, transportation from stores to location of CNG stations. | - | - |  | - |  | -
1.1 | 1”OD X 0.120” min Wall thk. SS Tube | RM | 0 | 0 | 0
1.2 | ¾”OD X 0.095” min Wall thk. SS Tube | RM | 800 | 200 | 1600 | 0 | 0
1.3 | ½”OD X 0.083” min Wall thk. SS Tube | RM | 100 | 25 | 200 |  | 0
1.0 (b) | SUPPLY OF SS TUBES as per Technical Specification (Make:Sandvik/Tubacex/Ratnamani) | - |  | 0 | 0
1.1 | 1”OD X 0.120” min Wall thk., Material SS316 SS Tube | M | 280 | 70 | 560 |  | 0
1.2 | ¾”OD X 0.095” min Wall thk., Material SS316SS Tube | M | 800 | 200 | 1600 |  | 0
1.3 | ½”OD X 0.083” min Wall thk., Material SS316 SS Tube | M | 100 | 25 | 200 |  | 0
| Note: Quantities beyond mentioned quantities may be provided as free issue. | - |  | 0 | 0
|  |  |  | 0 | 0
2 | Supply of SS Fittings (Make:Swagelok/Parker/SSP/Dk-lok/Hylok) | - |  | 0 | 0
| Quick Connect Body & Stem | - |  | 0 | 0
2.1 | End connection:½" Tube OD, for stem & ½”NPT (F) for body Material : SS316; Rated pressure : 5000 PSI @ 70°F Temperature: 0°F to 400°F | Nos. | 0 | 1 | 8 |  | 0
| Union | - |  | 0 | 0
2.2 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 160 | 40 | 320 |  | 0
2.3 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.4 | Size : 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 56 | 14 | 112 |  | 0
| Reducing Union | - |  | 0 | 0
2.5 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12 | 3 | 24 |  | 0
2.6 | Tube OD 1" x Tube OD ¾", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12 | 3 | 24 |  | 0
| Equal Tee | - |  | 0 | 0
2.7 | Size:½” OD x ½” OD x ½” OD, Material:SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12 | 3 | 24 |  | 0
2.8 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 12 | 3 | 24 |  | 0
2.9 | Size:1" OD x 1" OD x 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 4 | 1 | 8 |  | 0
| Nut | - |  | 0 | 0
2.1 | ¾ " OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.11 | ½" OD, Material : SS316 (Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.12 | 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
| Front Ferrule | - |  | 0 | 0
2.13 | 3/4" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.14 | ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.15 | 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
| Back Ferrule | - |  | 0 | 0
2.16 | 3/4" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.17 | ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
2.18 | 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 5 | 40 |  | 0
| Male Connector | - |  | 0 | 0
2.19 | Size ¼” NPT (M) x 3/8” OD, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 0 | 1 | 8 |  | 0
2.2 | Size 1/2” NPT (M) x 3/8” OD, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 0 | 1 | 8 |  | 0
|  |  |  | 0 | 0
3 | Supply of SS Ball Valves of Make:Swagelok/Parker/SSP conforming to MECON’s Technical Specification No. MEC/TS/05/62/048 for SS Ball Valves of following sizes, specifications as indicated below : | - |  | 0 | 0
|  |  |  | 0 | 0
3.1 | 2-Way Floating Normal Bore Ball Valve ¾" | Nos. | 36 | 9 | 72 |  | 0
3.2 | 2-Way Floating Normal Bore Ball Valve ½" | Nos. | 24 | 6 | 48 |  | 0
3.3 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection | Nos. | 0 | 0 | 0
3.4 | 2-Way Floating Normal Bore Ball Valve ¾" with 1" expander union on both sides | Nos. | 8 | 2 | 16 |  | 0
4 | Conductive Core Thermoplastic Hose (Make:SWAGELOK/PARKER/SYNFLEX/OPW) | - |  | 0 | 0
4.1 | 3/8” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling min. 3.0m length | Nos. | 0 | 1 | 8 |  | 0
|  |  |  | 0 | 0
| SECTION-B : ERECTION OF MECH. EQUIPMENT | - |  | 0 | 0
1.0 | Handling (including lifting and transportation from Client's store within city to CNG stations) and erecting in position, the following equipment on top of the compressor canopy or on the foundation or on roof at ~ 3 to 4 m above ground level. Contractor's scope includes supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, etc.. Scope also includes supply of all lifting tools / necessary accessories and hiring of cranes for same. | - |  | 0 | 0
1.1 | Cascade 4500/3000 water litre capacity. Erection on top of the compressor canopy ~ 3 to 4 m above ground level or on the foundation or on roof OF building at ~ 3 to 4 m above ground level | Nos. | 8 | 2 | 16 |  | 0
Note: | The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may increase or decrease at site at the time of actual execution and as per the discretion of Owner/ Engineer-in-charge. The unit rate shall be operated to work out the final payment due to Contractor. | - |  | 0 | 0
| SECTION-C : SUPPLY, ERECTION & COMMISSIONING OF MISCELLANEOUS ITEM | - |  | 0 | 0
1.0 | Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC | - |  | 0 | 0
1.1 | Air compressor pump (Tyre Inflator) | No. | 0 | 0 | 0
1.2 | Fire fighting Equipments | - |  | 0 | 0
1.2.1 | DCP -9 Kg | Nos. | 4 | 1 | 8 |  | 0
1.2.2 | DCP -75 Kg | Nos. | 4 | 1 | 8 |  | 0
1.2.3 | CO2 – 4.5 Kg | Nos. | 4 | 1 | 8 |  | 0
1.2.4 | Sand Bucket Stand with 4 Nos. Bucket | Nos. | 4 | 1 | 8 |  | 0
|  |  |  | 0 | 0
| SECTION-D : STRUCTURAL WORKS & PRESSURE GUAGES |  |  | 0 | 0
|  | - |  | 0 | 0
1 | Pipe Supports & Other Structures | - |  | 0 | 0
| Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-in-charge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). HDPE/ rubber sheet is to be provided between support & pipe wherever required., The work is to be completed in all respect as per scope of work and specification. | M.Ton. | 0.4 | 0.1 | 0.8 |  | 0
| Notes: | - |  | 0 | 0
i) | The quantities indicated above are tentative estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Owner/Owner representative. |  |  | 0 | 0
ii) | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates. |  |  | 0 | 0
iii) | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates. |  |  | 0 | 0
1.1 | PRESSURE GAUGES |  |  | 0 | 0
| Supply, installation and calibration of pressure Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG of WIKA / AN instruments etc. | No. | 4 | 1 | 8 |  | 0
TOTAL FOR MECHANICAL WORKS

## DBS Elec
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DUAGHTER BOOSTER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG Daughter Booster Station in RO | Total Quantity for 8 nos. CNG Daughter booster station | Unit Rate | Total Amount Exclusive of GST for 8 nos. of CNG stations
|  |  | A | B | C | D=C*B
PART II-INSTRUMENTATION WORKS
SUPPLY
1 | 3.0 KVA, single phase input (230V± 10%) and single phase output (230 V±1%) commercial grade UPS with battery bank ( Sealed Maiintenance Free VRLA) etc. for 4.0 hours backup for critical load installations including intercoonnecting cables, battery stand, ACDB and all other accessories, complete in all respect including commissioning spares as per technical write up, drawing & datasheet attached. | Set | 1 | 8 |  | 0
2 | Supply of complete Electronic earthing system with necessary accessories like copper stranded conductor, Cu plates, Cu strips, GI strips, Funnel with wire Mesh, GI pipe, PVC conduit, bolts,nuts, concrete chamber with CI cover, coke/charcoal, salt & sand etc., as per technical write up, drawings, etc. | Nos. | 2 | 16 |  | 0
TOTAL FOR SUPPLY WORKS
ERECTION
1 | 3.0 KVA, single phase input (230V± 10%) and single phase output (230 V±1%) commercial grade UPS with battery bank ( Sealed Maiintenance Free VRLA) etc. for 4.0 hours backup for critical load installations including intercoonnecting cables, battery stand, ACDB and all other accessories, complete in all respect including commissioning spares as per technical write up, drawing & datasheet attached. | No. | 1 | 8 |  | 0
2 | Intallation, testing and commissioning of complete Electronic earthing system with necessary accessories like copper stranded conductor, Copper Plates, GI strips, Funnel with wire Mesh, GI pipe, PVC conduit, bolts, nuts, concrete chamber with CI cover, coke/charcoal, salt & sand etc., | No | 2 | 16 |  | 0
TOTAL FOR ERECTION WORKS
TOTAL FOR SUPPLY+ERECTION WORKS
Notes :
(i) | Above quantities are estimated quantities and may change during detail engineering as per site condition. Successful Tenderer shall supply the equipments, at the same rate, as per these change quantities. Payment shall be made as per quantities erected.
(ii) | Makes of all equipemnts shall be as per preferred make list. Items for which preferred makes are not indicated shall be provided only after approval of the make by owner / consultant.

## DRS CIVIL
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DECOMPRESSION SKID
Sl. No. | Description of Item | Unit | Quantity for 1 (one) no. De-compression unit installation | Total Quantity for 6 (six) nos. De-compression unit installations | Unit Rate | Total Amount exclusive of GST 6 (six) nos. De-compression unit installations (in Rs.)
|  |  | A | B | C | D=C*B
PART I-CIVIL WORKS
1 | Site clearance and Earth Work
1.1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including disposal of excavated earth for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport.Item also include cutting and removing of bushes /tress with 30m girth (to be measured at 1.0m above ground) etc. ( Approval of location of disposal from local authority is in scope of contractor.)
| All kinds of soil | Sqm | 220 | 1320 |  | 0
1.2 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan but upto depth of 3.0m) including dewatering of both ground and surface water in all season, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, strutting required for keeping earth in position etc. and packing cavities (wherever required) including disposal of excess excavated earth and stacking of required excavated earth, for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport. ( Approval of location of disposal from local authority to be in scope of contractor.)
| All kinds of soil | Cum | 165 | 990 |  | 0
1.3 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan but upto depth of 3.0m) including dewatering of both ground and surface water in all season, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, strutting required for keeping earth in position etc. and packing cavities (wherever required) including disposal of excess excavated earth and stacking of required excavated earth, for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport. ( Approval of location of disposal from local authority to be in scope of contractor.)
| Ordinary rock | Cum | 5 | 30 |  | 0
1.4 | Filling with available earth (excluding rock) free from vegetation in foundation or trenches or embankments in layers (each layer should not exceed 15 cm) including poking by rods, profusely watering, consolidating with surface vibrator, compacting to achieve soil proctor density of 98% , for all leads and lifts, all complete as per directions of Engineer - In - charge. | Cum | 125 | 750 |  | 0
1.5 | Earth work in filling with good quality imported earth from approved source in the layers of 150 mm and compacted up to 95% to its MDD and any plan dimension including all testing, watering, rolling each layer with 1/2 tonne roller or wooden or steel rammers, and every 3rd and top-most layer with power roller of minimum 8 tonnes and dressing / filling up ground depressions etc. complete in all respect as per scope of work, detailed construction drawings , as per technical specifications and directions of the Engineer-in-charge. | Cum | 10 | 60 |  | 0
2 | CEMENT CONCRETE
2.1 | Providing and laying in position ready mixed plain cement concrete below foundation,& flooring, trenching and mass concrete,coping etc curing with all leads and lifts as per direction of the Engineer - in - charge.
a | PCC 1:2:4(1 Cement:2 Coarse sand: 4 stone aggregate 20mm nominal size) | Cum | 5 | 30 |  | 0
b | PCC 1:3:6(1 Cement:3 Coarse sand: 6 stone aggregate 20mm nominal size) | Cum | 21 | 126 |  | 0
3 | REINFORCED CEMENT CONCRETE
3.1 | FORMWORK
A | Providing Centering and shuttering including strutting, propping etc. and removal of form work for all level.
1 | For Foundations, footings, base of columns, plinth Beam, trenches etc | Sqm | 25 | 150 |  | 0
2 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | Sqm | 30 | 180 |  | 0
3.2 | STEEL REINFORCEMENT
A | Supply and placing in position Steel reinforcement TMT grade Fe415/Fe500 for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all levels. Item also include the provision of necessary chairs and spacer and cost of binding wire etc complete. The chairs and spacer bars provided will not be measured for payment. | MT | 2.5 | 15 |  | 0
3.3 | RCC
A | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work in super structure such as colums,beams,walls,etc. cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads and at all levels, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work, including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. Cement content considered in this item is 330 kg/cum. Excess/ less cement used as per design mix is payable/ recoverable separately.
1 | For all works upto plinth level | Cum | 32 | 192 |  | 0
2 | For all works above plinth level upto floor v level | Cum | 13 | 78 |  | 0
3.4 | Providing and fixing factory made precast RCC perforated drain covers, having concrete of strength not less than M-25,of size 500x500x50mm, reinforced with 8mm dia c/c bothways T.M.T.hoop bars,including providing 50mm dia perforations @100 to125 mm c/c, including providing edge binding with M.S. flats of size 50mm x 1.6 mm complete, all as per direction of Engineer-in-charge. | Each | 40 | 240 |  | 0
4 | CC BLOCK work
4.1 | Providing and laying cement blocks (solid blocks)masonry with 200 mm thick blocks upto plinth level and super structure above plinth level up to top level of building in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work.
| Upto Plinth level | Cum | 5 | 30 |  | 0
| Above plinth level | Cum | 5 | 30 |  | 0
5 | FINISHING
5.1 | 12 mm cement internal plaster(1Cement :3 Coarse sand) on walls of all heights at all levels in perfect line and level | Sqm | 50 | 300 |  | 0
5.2 | Painting with APEX/Wheathershield make exterior paint with one coat of primer and two or more coat of approved paint on new work wherever required to achieve even shade and colour for all heights and levels. | Sqm | 240 | 1440 |  | 0
6 | STEEL WORK
6.1 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer and two coats of synthetic enamel using structural steel etc. as required.
6.2 | In gratings, frames, guard bar, ladder, railings, brackets, gates,insert plates,angle inserts,Y angles and similar works | Kgs | 100 | 600 |  | 0
6.3 | Providing and fixing in concrete at all levels and positions, bolts with nuts and washers, pipe sleeves etc. including painting the exposed surfaces with two coats of approved paint, providing grease to exposed area of bolts, welding wherever necessary, complete as per drawing, specifications and instruction of engineer in charge (PCC blocks, jigs and fixtures will not be paid extra) and protecting the same till final erection. | Kgs | 42 | 252 |  | 0
7 | FLOORING
7.1 | 52 mm thick cement concrete flooring with concrete hardener topping, under layer 40 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) and top layer 12 mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate 6 mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacturer’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete. | Sqm | 175 | 1050 |  | 0
8 | RCC precast Panelled compound wall
8.1 | Supplying and fixing precast RCC M30 panells (minimum 50mm thick) in grooved precast RCC M30 posts (minimum section 140mmx125mm) for compound wall upto 3.0 M height including excavation, PCC 1:3:6 encasing for the posts (minimum 600mmx600mmx750mm), shuttering, reinforcement etc complete as per drawing, specification and direction of the Engineer. (payment shall be made in sqm for the laid area above floor level) | Sqm | 115 | 690 |  | 0
9 | Paver Block
9.1 | Providing and laying paving of pre cast concrete interlocking pavers made of M30 grade concrete of 80mm thickness of approved pattern make, size, of compressive strength 300KG /sq cm. Paver blocks should be laid with sand cushion as required with a gap of 1.5mm between the blocks filled with sand including paving and curb gap to be filled with concrete of same grade of concrete pavers | Sqm | 100 | 600 |  | 0
10 | DISMANTLING/DEMOLISHING
10.1 | Demolishing of Cement Concrete (PCC)of all grades manually/ mechanical means including disposal of debris as directed by the Engineer. Debris shall be disposed outside the site and this shall be entirly Contractor's responsibility irrespective of any Lead. | Cum | 45 | 270 |  | 0
10.2 | Demolishing of RCC of all grades manually/ mechanical means including disposal of debris as directed by the Engineer. Debris shall be disposed outside the site and this shall be entirly Contractor's responsibility irrespective of any Lead. | Cum | 2 | 12 |  | 0
TOTAL FOR CIVIL WORKS

## DRS ELECT
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DECOMPRESSION SKID
Item No. |  | Description | Unit | Quantity for 1(one) no. De-compression unit installation | Total Quantity for 6(six) nos. De-compression unit installations | Unit Rate | Total Amount exclusive of GST 6 (six) nos. De-compression unit installations (in Rs.)
|  |  |  | A | B | C | D=C*B
PART II-ELECTRICAL WORKS
ELECTRICAL WORKS -SUPPLY
1 | Supply of lighting fixtures complete with mounting bracket, flame proof/non flame proof type LIght fixture,glands, lugs etc. including civil works with pipe inserts for cables and all associated works as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects.Make of all equipments shlal be as per approved make list |  | - | -
| a) | Street lighting pole 6mtr high GI octagonal pole complete with bracket, GI clamps for fixing flame proof control gear box as per tender drawing & tender specification . | No's | 5 | 30 |  | 0
| b) | 4 x 24 W Flame proof street light Ex-d type fixture with T5 lamp, control gear in cast alluminium allow LM6 enclosure and toughened glass cover. The encloser shall be of IP: 65 suitable for Zone 1& 2 gas group IIA & IIB with all accessories. (Similar to CGL model FSL 424 ) | No's | 5 | 30 |  | 0
| c) | FLP Junction box for terminating Loop in & Loop Out cable. | No's | 5 | 30 |  | 0
| d) | 16A Rotary Switch in FLP LM6 Aluminium alloy , IP 65 enclosure for controlling canopy light fittings. | No | 1 | 6 |  | 0
2 | Earthing pits comprising, 3.5 meter long 50 mm dia. GI pipe electrode, charcoal, salt, GI earthing conductor for interconnecting the electrodes,6mm thick CI checked plate for cover ,CI earth pit marker, erection accessories confirming to IS- 3043 and as per technical specification.It shall also include brick masonry chamber and all other civil works |  | Nos. | 5 | 30 |  | 0
3 | Galvanised (GI) earth conductor .
| a) | GI Strip (50X6) mm | Mtr. | 80 | 480 |  | 0
| b) | GI Strip (25X3) mm | Mtr. | 60 | 360 |  | 0
| c) | 16 sq.mm braded copper wire | Mtr. | 5 | 30 |  | 0
4 | Crocodile Clamp-Brass |  | No. | 1 | 6 |  | 0
5 | Supply of 1.1kV grade XLPE insulated, PVC sheathed ST2 , FRLS armoured Cables (conforming to IS:7098 and specification) of following sizes: |  | - | -
| a) | 4 x 16 mm2 A2XFY | Mtr. | 30 | 180 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Mtr | 100 | 600 |  | 0
6 | Supply of 1.1 Kv grade cable FLP,double compression type Brass cable glands as per Tender Specification for the following sizes of cables:
| a) | 4 x 16 mm2 A2XFY | Nos. | 3 | 18 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Nos. | 16 | 96 |  | 0
7 | Supply of 1.1 Kv grade cable with heavy duty crimping type Copper lugs etc as per Tender Speciifcation for the following sizes of cables:
| a) | 4 x 16 mm2 A2XFY | Nos. | 12 | 72 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Nos. | 64 | 384 |  | 0
8 | Supply of following sizes of class 'B' G.I.Pipe including all material and labour as per specification and drawings approved |  | - | -
| a) | 50 mm NB | Mtr. | 100 | 600 |  | 0
| b) | 80 mm NB | Mtr. | 50 | 300 |  | 0
9 | FLP LM6, Aluminium alloy, Junction Box suitable for termination of 2 Nos. of 4C X 16 sq.mm, A2XFY cable and one number of 4C X 2.5 Sq.mm FRLS A2XFY cable . |  | No. | 1 | 6 |  | 0
TOTAL FOR ELECTRICAL (SUPPLY) WORKS
ELECTRICAL WORKS - ERECTION
1 | Erection, Testing & Commissioning of of lighting fixtures complete with mounting bracket, flame proof/non flame proof type LIght fixture,glands, lugs etc. including civil works with pipe inserts for cables and all associated works as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects.Make of all equipments shlal be as per approved make list |  | - | -
| a) | Street lighting pole 6mtr high GI octagonal pole complete with bracket, GI clamps for fixing flame proof control gear box as per tender drawing & tender specification . | No's | 5 | 30 |  | 0
| b) | 4 x 14 W Flame proof street light Ex-d type fixture with T5 lamp, control gear in cast alluminium allow LM6 enclosure and toughened glass cover. The encloser shall be of IP: 65 suitable for Zone 1& 2 gas group IIA & IIB with all accessories. (Similar to CGL maodel FSL 424 or equivalent) | No's | 5 | 30 |  | 0
| c) | FLP Junction box for terminating Loop in & Loop Out cable. | No's | 5 | 30 |  | 0
| d) | 16A Rotary Switch in FLP LM6 Aluminium alloy , IP 65 enclosure for controlling canopy light fittings. | No | 1 | 6 |  | 0
2 | Erection, Testing and Commissioning of Earthing pits comprising, 3.5 meter long 50 mm dia. GI pipe electrode, charcoal, salt, GI earthing conductor for interconnecting the electrodes,6mm thick CI checked plate for cover ,CI earth pit marker, erection accessories confirming to IS- 3043 and as per technical specification.It shall also include brick masonry chamber and all other civil works |  | Nos. | 6 | 36 |  | 0
3 | Galvanised (GI) earth conductor .
| a) | GI Strip (50X6) mm | Mtr. | 80 | 480 |  | 0
| b) | GI Strip (25X3) mm | Mtr. | 60 | 360 |  | 0
| c) | 16 sq.mm braded copper wire | Mtr. | 5 | 30 |  | 0
4 | Crocodile Clamp-Brass |  | No. | 1 | 6 |  | 0
5 | Laying, Termination, Testing & Commissioning of 1.1kV grade XLPE insulated, PVC sheathed ST2 , FRLS armoured Cables (conforming to IS:7098 and specification) of following sizes: |  | - | -
| a) | 4 x 16 mm2 A2XFY | Mtr. | 30 | 180 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Mtr | 100 | 600 |  | 0
6 | Installation, Commissioning of 1.1 Kv grade cable double compression type Brass cable glands as per Tender Specification for the following sizes of cables:
| a) | 4 x 16 mm2 A2XFY | Nos. | 3 | 18 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Nos. | 16 | 96 |  | 0
7 | Installation, Commissioning of 1.1 Kv grade cable with heavy duty crimping type Copper lugs etc as per Tender Speciifcation for the following sizes of cables:
| a) | 4 x 16 mm2 A2XFY | Nos. | 12 | 72 |  | 0
| b) | 4 x 2.5 mm2 2XWY | Nos. | 64 | 384 |  | 0
8 | Erection, Testing & Commissioning of following sizes of class 'B' G.I.Pipe including all associated civil work with all material and labour as per specification and drawings approved . |  | - | -
| a) | 50 mm NB | Mtr. | 100 | 600 |  | 0
| b) | 80 mm NB | Mtr. | 50 | 300 |  | 0
9 |  | FLP LM6, Aluminium alloy, Junction Box suitable for termination of 2 Nos. of 4C X 16 sq.mm, A2XFY and one number of 4C X 2.5 Sq.mm FRLS A2XFY cable . | No. | 1 | 6 |  | 0
TOTAL FOR ELECTRICAL (Erection) WORKS
TOTAL FOR ELECTRICAL (SUPPLY+ERECTION) WORKS
Note for Electrical :
Above quantities are estimated quantities and may change during detail engineering as per site condition. Successful Tenderer shall supply the equipments, at the same rate ,as per these change quantities. Payment shall be made as per quantities erected.
Makes of all equipemnts shall be as per preferred make list.Items for which preferred makes are not indicated shall be provided only after approval of the make by owner / consultant.

## DRS MECH
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DECOMPRESSION SKID
Item No. | Description | Unit | Quantity for 1(one) no. De-compression unit installation | Total Quantity for 6(six) nos. De-compression unit installations | Unit Rate | Total Amount exclusive of GST for 6 (six) nos. De-compression unit installations (in Rs.)
|  |  | A | B | C | D=B*C
PART III- Mechanical & Tubing Works
| SECTION-A : SS TUBE LAYING & TESTING | - | - | - |  | -
1.0 (a) | Laying with PVC heavy duty tube clamp of Swagelok/Parker/DK-Lok/Vaishnavi Hydraulics/Vardhaman bearings/AK Industries, Pneumatic testing with Nitrogen at 280 bar and commissioning of SS tubes along with fittings and valves as given below and as per Technical Specification and scope of work including handling, lifting, transportation from stores to location of De-compression unit stations. | - | - | - |  | -
1.1 | ¾”OD X 0.095” min Wall thk. SS Tube | RM | 25 | 150 |  | 0
1.2 | ½”OD X 0.083” min Wall thk. SS Tube | RM | 5 | 30 |  | 0
1.0 (b) | SUPPLY OF SS TUBES as per Technical Specification (Make:Sandvik/Tubacex/Ratnamani) | - | - | -
1.1 | ¾”OD X 0.095” min Wall thk.,Material SS316SS Tube | M | 25 | 150 |  | 0
1.2 | ½”OD X 0.083” min Wall thk.,Material SS316 SS Tube | M | 5 | 30 |  | 0
| Note: Quantities beyond mentioned quantities may be provided as free issue. | - |  | -
2 | Supply of SS Fittings (Make:Swagelok/Parker/SSP/Dk-lok/Hylok) | - |  | -
| Quick Connect Body & Stem | - |  | -
2.1 | End connection:½" Tube OD, for stem & ½”NPT (F) for body Material : SS316; Rated pressure : 5000 PSI @ 70°F Temperature: 0°F to 400°F | Nos. | 1 | 6 |  | 0
| Union | - |  | -
2.2 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 60 |  | 0
| Reducing Union | - |  | -
2.3 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 2 | 12 |  | 0
| Equal Tee | - |  | -
2.4 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1 | 6 |  | 0
| Nut | - |  | -
2.5 | ¾ " OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 2 | 12 |  | 0
| Front Ferrule | - |  | -
2.6 | 3/4" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 2 | 12 |  | 0
| Back Ferrule | - |  | -
2.7 | 3/4" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 2 | 12 |  | 0
| Male Connector | - |  | -
2.8 | Size 1/4” NPT (M) x 3/8” OD, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1 | 6 |  | 0
2.9 | Size 1/2” NPT (M) x 3/8” OD, SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1 | 6 |  | 0
Cross
2.10 | 3/4" OD X 3/4” X 3/4" OD X3/4" OD Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 1 | 6 |  | 0
3 | Supply of SS Ball Valves of Make:Swagelok/Parker/SSP conforming to MECON’s Technical Specification for SS Ball Valves of following sizes, specifications as indicated below : | - |  | -
3.1 | 2-Way Floating Normal Bore Ball Valve ¾" | Nos. | 4 | 24 |  | 0
3.2 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection | Nos. | 1 | 6 |  | 0
4 | Conductive Core Thermoplastic Hose (Make:SWAGELOK/PARKER/SYNFLEX/OPW) | - |  | -
4.1 | 3/8” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling min. 3.0m length | Nos. | 1 | 6 |  | 0
| SECTION-B : ERECTION OF MECH. EQUIPMENT | - |  | -
1.0 | Handling (including lifting and transportation from Client's store within city to location of Decompression unit) and erecting in position, the following equipment on the foundation . Contractor's scope includes supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, etc.. Scope also includes supply of all lifting tools / necessary accessories and hiring of cranes for same. | - |  | -
1.1 | Cascade 4500/3000 water capacity. Erection on foundation | Nos. | 1 | 6 |  | 0
Note: | The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may increase or decrease at site at the time of actual execution and as per the discretion of Owner/ Engineer-in-charge. The unit rate shall be operated to work out the final payment due to Contractor. | - |  | -
| SECTION-C : SUPPLY, ERECTION & COMMISSIONING OF MISCELLANEOUS ITEM | - |  | -
1.0 | Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the location of Decompression unit) as directed by EIC | - |  | -
1.1 | Fire fighting Equipments | - |  | -
1.1.1 | DCP -9 Kg | Nos. | 3 | 18 |  | 0
1.1.2 | CO2 – 4.5 Kg | Nos. | 2 | 12 |  | 0
1.1.3 | Sand Bucket Stand with 4 Nos. Bucket | Nos. | 1 | 6 |  | 0
SECTION-D : SUPPLY, ERECTION OF STRUCTURAL WORKS
1 | Pipe Supports & Other Structures | - |  | -
| Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-in-charge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). HDPE/ rubber sheet is to be provided between support & pipe wherever required., The work is to be completed in all respect as per scope of work and specification. | M.Ton. | 0.1 | 0.6 |  | 0
| Notes: | - | - | -
i) | The quantities indicated above are tentative estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Owner/Owner representative.
ii) | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates.
iii) | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates.
| TOTAL FOR MECHANICAL WORKS | Total Amount in INR (inclusive of all taxes & duties except GST)

## DRS STRL
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
DECOMPRESION SKID
Item No. | Description | Unit | Quantity for 1(one) no. De-compression unit installation | Total Quantity for 6(six) nos. De-compression unit installations | Unit Rate | Total amount exclusive of GST for 6 nos decompression skids
|  |  | A | B | C | D=C*B
PART IV : STEEL STRUCTURAL WORKS
ST-1 | Structural Steel Works for unloading platform & Other Allied Structures
| Supply of steel consisting of Plates, Rolled steel joists, Channels, Angles, Tubes, Rectangular / Square Hollow Steel sections, Fascia, Flashings, Rain water pipe & Gutter etc, straightening of raw steel if required . Preparation of all necessary Fabrication drawings ( Based on MECON Design drawings ) including bill of materials . Fabrication of Steel structures as per Fabrication drawings (including preparation of supplementary sketches and detailed bill of materials ) supply of bolts, nuts, washers , shims, packs, putty, gas, welding electrodes and all other consumables, as required. Cleaning and preparation of all steel surfaces by Mechanical Cleaning to St 3 of Swedish Standard for painting , Supply and application of One Coat of Primer Paint of Zinc Phosphate in Phenolic Alkyd medium 40 microns DFT, Intermediate Primer Coat of Zinc Phosphate in Phenolic Alkyd medium 40 microns DFT, One Coat of Intermediate Paint of Synthetic MIO ( ie: Micaceous Iron Oxide) 75 microns DFT, supply and application of 2 coats of Finishing paint Synthetic Enamel 25 microns DFT / coat. Finishing Coat shall be applied one Coat before erection and one coat after erection . The total thickness of paint shall be 205 Microns. Loading , Transportation and Unloading and Delivery at erection site of all fabricated structures up to height of about 12 M, erection, alignment and welding of all structures true to line, level, plumb and dimension, including rectification if any, splicing , site assembly all as per technical specifications and drawings, touch up painting, including supply of paint, where paint is damaged. | Tons | 0.5 | 3 |  | 0
ST-2 | Structure Steel Works for Miscellaneous Structures like Grating, Handrails, Hoardings etc
| Supplying, Fabricating & Erecting in position steel structures fabricated out of MS Girders, channels, Tees, angle, flats, plate, square hollow sections pipes etc. conforming to IS:2062 and/or from pipes conforming to IS:1161 for structural purpose for cascade supporting structure, loading/unloading platform, Gratings for platform, catladder,handrails, hoardings for sinages,Lcv stand, etc. of any size/dia for required design including cutting, welding, bolting, hoisting, fixing in position, including application of one coat of primer at shop and second coat of primer at site after erection and two coats of finishing paint at site .The work is to be completed in all respect as per specification ,scope of work, detailed construction drawings and directions of the Engineer-in-charge. | KG | 85 | 510 |  | 0
[ Rate to include cost of all labour, nut, bolts, tools, tackles, hire charges royalties, levies, transportation, scrap value, gas cutting, welding, other consumables, paints, compressed air, water, electric power etc. all complete.]
ST-3 | Providing and fixing Fencing Gates
Supplying, fabricating & fixing fencing gates fabricated from pipes conforming to IS:1161 and plates conforming to IS:2062 & fixing of GI weldmesh made from 3mm GI wire @ 75 mm bothways to structural steel frame by means of welding/bolting, painting with enamel paint in approved shade including supply of all raw materials, bolts, electrodes, transportation etc complete as per enclosed sketch, technical specifications and directions of the Engineer-In-Charge.
a) | 4m Wide x 2.1m High | Nos. | 1 | 6 |  | 0
ST- 4 | Providing and Fixing 6 O/P Chequered Plate Covers
| Providing and fixing chequered plate in approved panel or over steel structure including cutting, welding, hoisting, fixing in position, and applying two or more coats of approved quality synthetic enamel over a priming coat of approved steel primer etc complete as per scope detailed drawings , technical specifications and directions of the Engineer-In-Charge. | KG | 85 | 510 |  | 0
[Rate to include cost of all labour, nut, bolts, stiffening sections, bars tools, tackles, hire charges, royalties, levies, transportation, scrap value, gas cutting, welding, other consumables, paints, compressed air, water, electric power etc. all complete.]
Notes:
1 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all materials such as structural steel, purlins, nuts, bolts, washers, screws, seals, wire ropes,flashing,fitting and fixtures,gutter, rain water pipes and bends, electrodes, edge colour coated sheets for signage works,primer, paint and all consumables etc. with all bye works and sundry works complete in all respect.
2 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser.
3 | The cost of MS bolts (permanent and service), washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants, etc., as required for the work shall be deemed to be included in the quoted rates.
4 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accordance with Time schedule, are deemed be included in the quoted rates.
5 | All accessories like MS tower bolts, MS Pivot, MS Wheels, MS Tee section, locking arrangement etc. shall be measured by weight only.
6 | Contractor shall ensure proper alignment and smooth operation of Gate.
| TOTAL FOR STRUCTURAL WORKS | Total Amount in INR (inclusive of all taxes & duties except GST)
0

## CNG CIVIL
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3 (Three) nos. of CNG mother station | Unit Rate | Total Amount exclusive of GST for 3 (Three) nos. of CNG mother station (in Rs.)
|  |  | A | B | C | D=C*B
PART - I : CIVIL WORKS
1 | Site clerance and earth Work | -
| Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including disposal of excavated earth for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport.Item also include cutting and removing of bushes /tress with 30m girth (to be measured at 1.0m above ground) etc. (Approval of location of disposal from local authority is in scope of contractor.) | -
1.1 | All kinds of soil | Sqm | 1035 | 3105 |  | 0
2 | Felling of trees of the girth (measured at a height 1 m above ground level ) including cutting of trunks and branches , removing the roots and stacking of serviceable materials and disposal unserviceable material. | - |  | 0
2.1 | a) beyond 30 cm Girth upto and including 60 cm girth | Each | 6 | 18 |  | 0
3 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan but upto depth of 3.0m) including dewatering of both ground and surface water in all season, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, strutting required for keeping earth in position etc. and packing cavities (wherever required) including disposal of excess excavated earth and stacking of required excavated earth, for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport. ( Approval of location of disposal from local authority to be in scope of contractor.) | - |  | 0
3.1 | All kinds of soil | Cum | 1955 | 5865 |  | 0
3.2 | same as above but beyond 3.0m in depth | Cum | 90 | 270 |  | 0
4 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan but upto depth of 3.0M) including dewatering of both ground and surface water in all season, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, strutting required for keeping earth in position etc. packing cavities (wherever required) including disposal of excess excavated earth and stacking of required excavated earth, for all leads and lifts, Excavated portion to be neatly rammed, leveled, dressed & compacted to receive bed concrete.Carting away excess excavated earth / debris as directed by the project manager outside the premises to any place designated by the local authority from site by mechanical transport. ( Approval of location of disposal from local authority to be in scope of contractor.) | - |  | 0
4.1 | Ordinary Rock | Cum | 40 | 120 |  | 0
4.2 | same as above but beyond 3.0m in depth | Cum | 23 | 69 |  | 0
4.3 | Hard Rock (Blasting Prohibited) | Cum | 23 | 69 |  | 0
4.4 | same as above but beyond 3.0m in depth | Cum | 12 | 36 |  | 0
5 | Earth filling from available earth (excluding rock) under floors and other places with special compaction to achieve dry density of 95% standard proctor density with excavated surplus earth including cost of excavation reclaiming from spoil heaps within plant site as per instruction of the Consultant at all heights/depths, transporting, depositing, compacting and dressing, trimming complete as desired in layers not exceeding 15 cms including watering, consolidating by mechanical means as per specifications and instructions of the Consultant. | Cum | 805 | 2415 |  | 0
6 | Earth work in filling with good quality imported earth from approved source in the layers of 150 mm and compacted up to 95% to its MDD and any plan dimension including all testing, watering, rolling each layer with 1/2 tonne roller or wooden or steel rammers, and every 3rd and top-most layer with power roller of minimum 8 tonnes and dressing / filling up ground depressions etc. complete in all respect as per scope of work, detailed construction drawings , as per technical specifications and directions of the Engineer-in-charge. | Cum | 290 | 870 |  | 0
7 | Supplying and filling in foundation and plinth with river sand under floors for all leads and lifts, including watering, ramming, consolidating and dressing complete. | Cum | 23 | 69 |  | 0
8 | Providing and injecting chemical emlusions for pre-construction anti-termite treatement and creating continious chemical barrier under and all round the column pits, wall trenches, excavation top surface of plinth filling, junction, external perimeter of buildings, expamsion joins surrounding of pipes and conduit etc. complete. (plinth area of the building at ground level shall only be measured) with chlorpyriphos/Lindance E.C. 20% with 1% concentration.Work to be executed by approved agency and specified guarantee for 07 years shall be furnished by the tenderer. | Sqm | 90 | 270 |  | 0
0
9 | CEMENT CONCRETE | - |  | 0
| Providing and laying in position ready mixed plain cement concrete below foundation,& flooring, trenching and mass concrete,coping etc including shuttering ,curing with all leads and lifts as per direction of the Engineer - in - charge. | - |  | 0
9.1 | PCC 1:2:4 (1 Cement: 2 Coarse sand: 4 Stone aggregate 20mm nominal size) | Cum | 20 | 60 |  | 0
9.2 | PCC 1:3:6 (1 Cement: 3 Coarse sand: 6 Stone aggregate 20mm nominal size) | Cum | 100 | 300 |  | 0
9.3 | PCC 1:4:8 (1 Cement: 4 Coarse sand: 8 Stone aggregate 20mm nominal size) | Cum | 12 | 36 |  | 0
| DAMP-PROOF COURSE (DPC) | - |  | 0
10 | Providing and laying damp proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggreate 20mm nominal size) including providing and mixing of water proofing compound @ 2% of cement content and providing and applying two layers of bitumen of grade 80/100 of approved quality using 1.7 kg/ sqm on damp proof course after cleaning the surface with brushes and finally with a piece of cloth likely soaked in kerosene oil complete and as directed by the Project Manager. | Sqm | 18 | 54 |  | 0
| REINFORCED CEMENT CONCRETE | -
| FORMWORK | -
11 | Providing Centering and shuttering including strutting, propping etc. and removal of form work for all level. | -
11.1 | For Foundations, footings, base of columns, plinth Beam etc | Sqm | 920 | 2760 |  | 0
11.2 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | Sqm | 465 | 1395 |  | 0
11.3 | Suspended floors, roofs, landings, balconies and access platform ,lintels etc. | Sqm | 270 | 810 |  | 0
11.4 | Columns, Pillars, Piers, Abutments, Posts and Struts | Sqm | 230 | 690 |  | 0
| STEEL REINFORCEMENT | -
12 | Supply and placing in position Steel reinforcement TMT grade Fe415/Fe500 for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all levels. Item also include the provision of necessary chairs and spacer and cost of binding wire etc complete. The chairs and spacer bars provided will not be measured for payment. | -
12.1 | Thermo-Mechanically Treated bars | MT | 44 | 132 |  | 0
13 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work in super structure such as coloums, beams, walls, etc cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads and at all levels, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work, including pumping of R.M.C. from transit mixer to site of laying, excluding the cost of centering, shuttering finishing and reinforcement, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. Cement content considered in this item is 330 kg/cum. Excess/ less cement used as per design mix is payable/ recoverable separately. | -
13.1 | For all works upto plinth level | Cum | 315 | 945 |  | 0
13.2 | For all works above plinth level upto floor v level | Cum | 75 | 225 |  | 0
14 | Add/deduct for using extra /less cement in the items of design mix over and above the specified cement content therein. | Kgs | 2300 | 6900 |  | 0
| CC BLOCK work | -
15 | Providing and laying cement blocks (solid blocks) masonry Grade M 7.5 with 200 mm thick blocks upto plinth level and super structure above plinth level up to top level of building in cement mortar 1:4 (1 cement : 4 coarse sand ). | -
15.1 | Upto Plinth level | Cum | 105 | 315 |  | 0
15.2 | Upto floor V level | Cum | 90 | 270 |  | 0
16 | Brick work with bricks of class designation 5.0 with Mortar 1:6 (1Cement: 6 Coarse sand) in all levels. | Cum | 25 | 75 |  | 0
17 | Providing and fixing 75 mm thick M-25 factory made RCC drain/trench cover including cost of shuttering and minimum reinforement@ 8mm dia TMT Fe-500 bars @100mm c/c bothway. The RCC cover shall be encased with 100mm wide 1.6mm thick MS sheet alongwith 2 nos 12mm dia bar for hook etc complete including painting of MS sheet . | Sqm | 90 | 270 |  | 0
17.1 | Providing and fixing 100mm thick M-25 factory made RCC drain/trench cover including cost of shuttering and minimum reinforement@ 8mm dia TMT Fe-500 bars @100mm c/c bothway in two layers. The RCC cover shall be encased with 100mm wide 1.6mm thick MS sheet alongwith 2 nos 12mm dia bar for hook etc complete including painting of MS sheet . | Sqm | 160 | 480 |  | 0
| STONE CLADDING WORKS | -
18 | Providing and fixing Granite Stone gang saw cut (mirror polished and machine cut) of thickness 18 mm for wall lining, dispenser pedestal, platform, counter, staircase etc including nosing etc., backing filled with a grout of average 12-15 mm thick in cement mortar 1:3 (1 cement : 3 coarse sand), including pointing with white cement mortar 1:2 (1 white cement : 2 marble dust) with an admixture of pigment to match the granite shade .(Basic rate of Granite : Rs1500/sqm). | Sqm | 18 | 54 |  | 0
| STEEL WORK | -
19 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 - part 1 and M.S. top cover of required thickness for rolling shutters. | -
| 80 x1.25 mm M.S. laths with 1.25 mm thick top cover including Providing and fixing ball bearing for rolling shutters and providing mechanical device chain and crank operation for operating rolling shutters for all sizes and at all levels including two coats of approved quality synthetic enamel paint over a coat of primer. | Sqm | 12 | 36 |  | 0
20 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying two coats of approved quality Synthetic enamel paint over a primer coat using structural steel etc. as required. | -
20.1 | In gratings, frames, guard bar, ladder, railings, brackets, gates, insert plates, angle insets incuding Y anges and similar works including two coats of approved quality Synthetic enamel paint over a primer coat. | Kgs | 7245 | 21735 |  | 0
20.2 | Providing and fixing MS tube hand rail of approved size by welding etc to steel ladder railing, balcony railing, staircase railing and similar works, including two coats of approved quality Synthetic enamel paint over a primer coat. | Kgs | 345 | 1035 |  | 0
21 | FLOORING | -
| Providing and laying R.C.C. vacuum dewatering concrete flooring with floor hardener of approved make to be sprinkeled at the rate of 5 kg/sqm before mechanical troweeling as per manufacturer's specifications including mixing, tamping mechanically, consolidating, leveling cement concrete of grade M25 in grade slab, 200/150 thick including suction drying, mechanical trowelling (power float) and finishing, curing, cutting expansion grooves and filling expansion grooves with polysulphide joint fillers complete as specified and directed including shuttering but excluding reinforcement, including doweled construction joints as per drawings. | Cum | 105 | 315 |  | 0
22 | 52 mm thick cement concrete flooring with concrete hardener topping, under layer 40 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) and top layer 12 mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate 6 mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacturer’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete. | Sqm | 14 | 42 |  | 0
23 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS:15622 (thickness to be specified by the manufacturer), of approved make,in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | sqm | 30 | 90 |  | 0
24 | Providing and laying rectified Glazed Ceramic floor tiles of size 300x300 mm or more (thickness to be specified by the manufacturer), of 1st quality conforming to IS : 15622, of approved make, in approved colours, laid on 20 mm thick cement mortar 1:4 (1 Cement: 4 Coarse sand), including grouting the joints with white cement and matching pigments etc., complete. | sqm | 10 | 30 |  | 0
25 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600 x 600 mm | Sqm | 35 | 105 |  | 0
| ROOFING | -
26 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. sheet 1 m x1 m x 400 micron, finished with 12 mm cement plaster 1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete. | Each | 4 | 12 |  | 0
27 | Providing and laying integral cement based water proofing treatment including preparation of surface as required for treatment of roofs, balconies, terraces etc consisting of following operations: a) Applying a slurry coat of neat cement using 2.75 kg/sqm of cement admixed with water proofing compound conforming to IS. 2645 and approved by Engineer-in-charge over the RCC slab including adjoining walls upto 300 mm height including cleaning the surface before treatment. b) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115 mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs c) After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed jointless cement mortar of mix 1:4 (1 cement :4 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge including laying glass fibre cloth of and approved by Engineer-in-charge including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3 mm deep. e) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test. All above operations to be done in order and as directed and specified by the Engineerin-Charge :Work to be executed by approved agency and specified guarantee for 07 years shall be furnished by the tenderer. | -
27.1 | With average thickness of 120 mm and minimum thickness at khurra as 65 mm. | Sqm | 100 | 300 |  | 0
28 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion complete with PVC moulded fittings and accessories like Couplers, Tees, Bends, Shoes, PVC pipe clamps & fastner complete in all respects and as directed by Engineer-in- Charge | -
| 110 mm diameter | Rm | 12 | 36 |  | 0
29 | FINISHING | -
29.1 | 12 mm cement internal plaster on walls of all heights at all levels in perfect line and level | Sqm | 275 | 825 |  | 0
29.2 | 18 mm external cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement: 5 coarse sand) and a top layer 6 mm thick cement plaster 1:5 (1 cement : 5 fine sand) for all heights and levels in perfect line and level | Sqm | 1035 | 3105 |  | 0
29.3 | 6 mm cement plaster of mix : | -
| 1:3 (1 cement : 3 fine sand) in ceiling in perfect line and level at all levels | Sqm | 95 | 285 |  | 0
29.4 | 15mm thick Cement plaster 1:6 (1Cement : 6 coarse Sand) outer walls | Sqm | 870 | 2610 |  | 0
29.5 | Wall painting with premium acrylic emulsion paint, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre, of approved brand and manufacture, including applying two or more coats wherever required, to achieve even shade and colour for all heights and levels.Item includes applying pop putty and one coat of primer. | Sqm | 290 | 870 |  | 0
29.6 | Painting with synthetic enamel paint, having VOC (Volatile Organic Compound) content less than 150 grams/ litre, of approved brand and manufacture, including applying two or more coats over a coat of primer wherever required to achieve even shade and colour for all heights and levels | Sqm | 175 | 525 |  | 0
29.7 | Painting with APEX/Wheathershield make exterior paint with one coat of primer and two or more coat of approved paint on new work wherever required to achieve even shade and colour for all heights and levels | Sqm | 1150 | 3450 |  | 0
30 | ALUMINIUM WORK | -
| Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. | -
| Anodised alumunium (anodised as per IS:1868 of required shade and coating as per AC-15) | -
30.1 | For fixed portion such as frame etc | Kgs | 230 | 690 |  | 0
30.2 | For shutter of door window etc | Kgs | 175 | 525 |  | 0
31 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. | -
31.1 | Pre-laminated particle board with decorative lamination on one side and balancing lamination on other side | Sqm | 12 | 36 |  | 0
32 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315, having brand logo embossed on the body / plate with double spring mechanism and door weight upto 125 kg, for doors, including cost of cutting floors, embedding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge | -
32.1 | With stainless steel cover plate minimum 1.25 mm thickness | Each | 6 | 18 |  | 0
33 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): | -
33.1 | With float glass panes of 5.50 mm thickness | Sqm | 12 | 36 |  | 0
34 | Providing & fixing colour coated aluminium hardware fittings with approved quality and shade as per IS specifications/as approved by Consultant to woodwork with cadmium plated MS screws, suitable sockets in masonry/concrete surface if required including all bye-works complete as per specification, drawing and instruction of Consultants (fittings shall not be paid separately in composite items which specify inclusions of fittings)
| a) Butt hinges (extruded section 125 mm x 75 mm x 4 mm) | Nos | 25 | 75 |  | 0
b) Tower bolts (with barrel & bolts of extruded section -
| (i) 200 mm x 10 mm | Nos | 10 | 30 |  | 0
c) Sliding door bolts including locking arrangement (aldrop)
| (i) 250 mm long x 16 mm dia rod | Nos | 8 | 24 |  | 0
d) Grip handle without back plate of approved IS brand
| (i) 125 mm long | Nos | 20 | 60 |  | 0
34 | e) floor stopper of double type for door shutters up to 40 mm thick
| (i) rubber - double type | Nos | 10 | 30 |  | 0
| f) Providing & fixing approved quality hydraulic door closer conforming to IS:3564 (Everite or equivqlent) as directed by Consultant | Nos | 2 | 6 |  | 0
35 | ROAD WORK & External development | -
35.1 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge).SIZE : (150MMX600MM) | Cum | 12 | 36 |  | 0
35.2 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earth with lead upto 50 metres. | Sqm | 1380 | 4140 |  | 0
35.3 | Extra for compaction of earth work in embankment under optimum moisture conditions to give at least 98% of the maximum dry density (proctor density). | Cum | 175 | 525 |  | 0
35.4 | Providing and laying 10-40mm well graded granular stone aggregate for wet mix macadam as base course compacted thickness 135mm done in two layers (each layer compacted from 200 mm to 135 mm) including all materials, labours, plant and machinary includinng all lead and lift, loading, unloading, transporting, stacking, spreading to line, level gade and camber, compacting, watering etc., complete with vibratory roller compactor 8 to 10 tonne to attain 98% of max. dry density | Cum | 90 | 270 |  | 0
35.5 | Construction of dry lean cement concrete sub base over a prepared sub-grade with coarse and fine aggregate conforming to IS:383, the size of coarse aggregate not exceeding 25 mm, aggregate cement ratio not to exceed 15:1, aggregate gradation after blending to be as per specifications, cement content not to be less than 150kg/cum optimum moisture content to be determined during trial length construction, concrete strength not to be less than 10 Mpa at 7 days, mixed in a batching plant, transported to site, for all leads & lifts, laid with a mechanical paver, compacting with 8-10 tonne vibratory roller, finishing and curing etc. complete as per direction of Engineer-in- charge. | Cum | 130 | 390 |  | 0
35.6 | Providing and laying paving of pre cast concrete interlocking pavers made of M30 grade concrete of 80mm thickness of approved pattern make, size, of compressive strength 300KG /sq cm. Paver blocks should be laid on 150mm thk DLC and sand cushion as required with a gap of 1.5mm between the blocks filled with sand including paving and curb gap to be filled with concrete of same grade of concrete pavers | Sqm | 370 | 1110 |  | 0
36 | WATER SUPPLY & SANITARY | -
| Providing and fixing PVC water tank of approved make with ISI mark and conforming to IS 12701 and with GI fittings for inlet, outlet, Over flow, scour float valve, connections of required size and dia. Including connections and hoisting/fixing the same tank on roof and other places at all heights with all bye-works complete at all leads and lifts as per drawings, specifications and instructions of the Engineer Incharge. (Support of tank on brick/RCC/PCC will be paid under relevant items) | -
36.1 | a) 1000 litres capacity | Nos | 2 | 6 |  | 0
37 | Providing and fixing white glazed vitreous china European water closet with ISI mark - Studio type with cistern (EWC) of superior quality 81cm high, double trap syphonic pattern, 'P' or 'S' trap, with low level cistern with cover with siphon and standard flush fittings, plastic seat cover & lid of superior approved quality, CP brass bar hinges, screws, bolts, rubber, buffers 15mm dia PVC inlet pipe connection and CP brass angle stopcock, fixing EWC to floor with floor trap for waste water and necessary brass screws, all complete at all leads and lifts as per manufacturer's specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
38 | Supplying, fitting and fixing white glazed vitreous china wash basin of superior quality - HSW No. 10032 model or equivalant with ISI mark and size 550mm x 430mm, having single or double holes with 15 mm CP brass pillar tap - JAQUAR Continental series No. 011, CP brass chain and plugs, 32mm CP brass waste coupling, PVC flexible waste pipe, 15mm PVC inlet water pipe connection, CI cantilever brackets embedded in 1:2:4 concrete, 15 mm CP brass angle stopcock - JAQUAR Continental series No. 053, etc. filling the gaps between basin and wall with white cement etc. all complete at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
39 | Supplying, fabricating and laying UPVC pipes BS 5255 including collars, bends and specials, taking out waste water and soil waste from toilets to the nearest gully trap or inspection chamber including the cost of all material, labour, leads & lifts, transportation, taxes, duties, all as per specifications, drawings and directions of the Engineer-In-charge. | -
39.1 | a) 75 mm dia | RM | 65 | 195 |  | 0
39.2 | b) 110 mm dia | RM | 12 | 36 |  | 0
39.3 | c) 160 mm dia | RM | 25 | 75 |  | 0
39.4 | Supply and fixing of Floor trap with SS grating to waste water pipe connection. | -
| 1) 75mm dia of weight not less than 4.8 Kgs. | Nos | 3 | 9 |  | 0
40 | Providing and fixing white glazed vitreous china large flat back, channel flushing, front lipped standing urinal size 590x375x390mm of superior quality from approved make (similar to HSW No. 60002 model with ISI mark,with push valve, 15 mm PVC flexible inlet connection, 15mm CP brass angle cock, 15mm dia CP brass spreaders connceted to matching connecting pipe from cistern and 32mm dia PVC waste pipe upto floor all as per directions of the Engineer-In-charge (partitions excluded). | Nos | 2 | 6 |  | 0
41 | Providing and fixing 15mm CP brass long body bib cock with wall flange - JAQUAR Continental series No. CON-047KN or equivalant at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
42 | Providing and fixing 15mm CP brass concealed stop cock (extra heavy body) with adjustable wall flange - JAQUAR Continental series No. CON-087KN or equivalant at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
43 | Providing and fixing 15mm CP brass angular stop cock - JAQUAR Continental series No. CON-059KN or equivalant at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
44 | Providing and fixing CP brass health faucet with 8mm dia, 1m long flexible tube and wall hook with NRV- JAQUAR Allied series No. ALD-CHR-577 or equivalant at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | Nos | 2 | 6 |  | 0
45 | Supplying, fitting and laying upvc solvent weld plumbing pipe conforming ASTM D-1785 with all necessary fittings such as bends, tees, elbows, reducers, unions, nipples, plugs, clamps, fixtures, etc., in masonry / concrete works etc., complete at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | -
45.1 | a) 50 mm nominal bore | RM | 15 | 45 |  | 0
45.2 | b) 40 mm nominal bore | RM | 15 | 45 |  | 0
45.3 | c) 32 mm nominal bore | RM | 100 | 300 |  | 0
45.4 | d) 25 mm nominal bore | RM | 20 | 60 |  | 0
45.5 | e) 20 mm nominal bore | RM | 15 | 45 |  | 0
45.6 | f) 15 mm nominal bore | RM | 15 | 45 |  | 0
46 | Providing minimum 6mm thick polished float glass mirror, bevelled edge, of approved make fixed to with 6mm thick marine plywood sheet backing with teakwood beading, fixing arrangements all complete at all leads and lifts as per drawings, specifications and instructions of the Engineer-In-charge. | -
| Mirror size- 750x450mm | Nos | 2 | 6 |  | 0
47 | Providing and fixing recessed toilet paper roll holder including roller white glazed vitreous china, HSW No. 40.025 or approved equivalent make | Nos | 2 | 6 |  | 0
48 | Providing and fixing CP brass towel rail 600mm long, 20 mm dia with CP brackets fixed to wall with SS screws and TW guttas. | Nos | 2 | 6 |  | 0
49 | Construction of brick masonry inspection chamber with full bricks, in CM 1:5, provided with a light duty CI covers conforming to IS:1726, 610 x 455 mm, weight not less than 52 kg, embedding the CI frame in 100 mm thick RCC top slab, neatly finished including 12mm thick plastering on both faces in CM 1:6, rounding, float coat of neat cement finish on the inner side, PCC bedding etc., all complete including excavtion and backfilling, shuttering, painting the frame and cover with two coats of approved anti corrosive paint etc., as per specifications and direction of Consultant.
| c) Internal size 450x450 | Nos | 3 | 9 |  | 0
50 | Providing yard gully trap 150x100mm with CI grating 150 x 150mm and water tight light weight CI covers conforming to IS:1726 of size 300x300mm including half-brick masonry in CM (1:4) plastered neatly with CM (1:4) on both faces, 100mm thick PCC bed of mark M-10C, necessary excavation, complete as per direction of the Consultant. | Nos | 2 | 6 |  | 0
51 | Supplying, fitting and fixing superior quality gun metal gate valve (full way) of "LEADER" make or equivalent with ISI mark
| a) 32mm dia | Nos | 2 | 6 |  | 0
| MISCELLANEOUS WORK | -
52 | Providing and laying manually or by pumping at all positions a ready mix non-shrink cementitious grout of compressive strength specified below for specified works e.g. base grouting of rotating equipment and other installation complete in all respects as per scope of work, detailed construction drawings , technical specifications and directions of the Engineer-In-Charge. | -
52.1 | a) Having compressive strength of 30 N/mm2 | Per bag of 25 Kg | 120 | 360 |  | 0
| [1) Approved makes are ACC, FOSROC, ROFF, SEIKA QUALCRETE. | -
| 2) Minimum coverage as per manufacturers recommendations shall be applied in absence of actual field consumption data.] | -
| 3. To be read in conjunction with relevent clause of PJS. | -
53 | Providing and fixing in concrete at all levels and positions, bolts with nuts and washers, pipe sleeves etc. including painting the exposed surfaces with two coats of approved paint, providing grease to exposed area of bolts, welding wherever necessary, complete as per drawing, specifications and instruction of engineer in charge (PCC blocks, jigs and fixtures will not be paid extra) and protecting the same till final erection. | Kgs | 450 | 1350 |  | 0
54 | Providing and fixing concertina coil fencing with punched tape concertina coil 600mm dia 10metre openable length(total length 90m) having 50 nos. rounds per 6 metre length, upto 3 m height of wall with existing angle iron 'Y' shaped placed 2.4 m or 3.00 m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal including necessary bolts or G.I. barbed wire tied to angle iron all complete as per direction of Engineer-in-charge with reinforced barbed tape (RBT)/ Spring core (2.5mm thick) wire of high tensile strength of 165 kg/sq.mm with tape (0.52 mm thick) and weight 43.478 gm/metre. (cost of M.S. angle, C.C.blocks shall be paid separately) | RM | 175 | 525 |  | 0
55 | supply and installation of high grade rubber and PVC made Speed Breakers at ingress and egress. Make, size and type shall be as per directions of Engineer-In-Charge | Nos. | 2 | 6 |  | 0
56 | Providing and mixing approved water proofing admixture as per the manufacturer's specification including cost of material complete with all byeworks as per drawing, manufacturer's specifications and instruction of the Engineer-In-charge. | per bag of 50kg cement used | 230 | 690 |  | 0
| a) Liquid water proofing compound of approved make (similar to Prolapin 421 IC/Plastocrete - N) | -
57 | Providing and laying stone ballast 40 to 115 mm size in layers upto 200mm thickness (wherever not covered in respective SOR items) with spreading & blinding material like sand, stone grit and compaction with mechanical means, watering etc. under floors/foundations, plinth protection & as per drawings including cost of material complete in all respect as per scope of work, detailed construction drawings as per technical specifications and directions of the Engineer-in-charge. | Cum | 14 | 42 |  | 0
58 | Providing and fixing G.I. chain link fabric fencing of required width in mesh size 50x50 mm including strengthening with 2 mm dia wire or nuts, bolts and washers as required complete as per the direction of Engineer-In-charge. The cost of structural steel and PCC shall be paid separately. | -
58.1 | Made of G.I. wire of dia 4 mm | Sqm | 120 | 360 |  | 0
59 | Supplying & Spreading of trap / granite /quartzite/gniss crusher broken stone metal of following size for the sub all lead & lift e.t.c. complete | -
| a) 40 mm metal | Cum | 4 | 12 |  | 0
| DISMANTLING/DEMOLISHING | -
60 | Demolishing of Cement Concrete (PCC) of all grades manually/mechanical means including disposal of debris as directed by the Engineer. Debris shall be disposed outside the site and this shall be entirly Contractor's responsibility irrespective of any Lead. | Cum | 5 | 15 |  | 0
61 | Demolishing of RCC of all grades manually/ mechanical means including disposal of debris as directed by the Engineer. Debris shall be disposed outside the site and this shall be entirly Contractor's responsibility irrespective of any Lead. | Cum | 15 | 45 |  | 0
62 | Demolishing of CC block work/brick work / stone masonry of all grades manually/ mechanical means including disposal of debris as directed by the Engineer. Debris shall be disposed outside the site and this shall be entirly Contractor's responsibility irrespective of any Lead. | Cum | 20 | 60 |  | 0
63 | Demolishing barbed wire or flexible wire rope in fencing including making rolls and staking as directed by the Engineer. | Kgs | 35 | 105 |  | 0
64 | SOAK PIT AND SEPTIC TANK | -
64.1 | Providing and construction of septic tank in brick masonry and base and top slab in RCC M25 complete in all respect as per scope of work, detailed construction drawings, technical specifications and directions of the Engineer-in-charge. | Nos. | 1 | 3 |  | 0
64.2 | Making soak pit with 2.5 m diameter 3.0 metre deep with 45 x 45 cm dry brick honey comb shaft with bricks and S.W. drain pipe 100 mm diameter, 1.8 m long complete as per standard design. With class7.5 bricks | Nos. | 1 | 3 |  | 0
64.3 | Supply and placing NP2 class R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of (1:2): With 150mm dia | RM | 60 | 180 |  | 0
65 | BORE WELL
Boring, drilling the borewell of 6.5 inch dia with casing/strainer pipe of approved make by suitable method prescribed in IS:2800 (P-I) with 300 mm dia PVC outer casing pipe till required depth including labour, hire and running charges of all equipment, tools, plants, machineries& fittings required for the job, supply and fixing required capacity submersible pump of approved make with electrical cabling &accessories,flushing & development of borewell, providing borewell water and yield test reports etc all complete as per direction of the Engineer.
65.1 | a) Drilling in all type of strata upto 100 Mtr depth. | RM | 100 | 300 |  | 0
| b) Drilling in all type of strata beyond 100 Mtr and upto 200 Mtr depth. | RM | 100 | 300 |  | 0
| c) Supplying and fixing in position in borewell UPVC casing pipe 7inch dia as per IS:12818 at all depths including fittings, accessories etc. | RM | 50 | 150 |  | 0
| d) Supplying and fixingin position Submersible pump of required capacity with electrical cables, fittings, fixtures etc.-3HP , 30 Stage Motor 259 to 702 feet : Head Ra... 1440 to 4320 ltrs/hrs : F... 4" OD, 1.25" Delivery Single Phase | Nos. | 1 | 3 |  | 0
TOTAL FOR CIVIL WORKS

## CNG ELEC
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3(Three) nos. of CNG mother station | Unit Rate | Total Amount for 3 (Three) nos. of CNG mother stations exclusive of GST (in Rs.)
|  |  | A | B | C | D=B*C
PART II-ELECTRICAL WORKS
ELECTRICAL WORKS -SUPPLY
1 | Supply of lighting fixtures complete with mounting bracket, flame proof/non flame proof type LIght fixture,glands, lugs etc. including civil works with pipe inserts for cables and all associated works as per specifications, drawings and instruction of Engineer-in-charge. Work to be completed in all respects.Make of all equipments shlal be as per approved make list | - | -
a) | Street lighting pole 6mtr high GI octagonal pole complete with bracket, GI clamps for fixing flame proof Junction Box, and other accessories as required as per standard drawing & tender specification. | Set | 12 | 36 |  | 0
b) | FLP Junction box for terminating Loop in & Loop Out cable. | Set | 12 | 36 |  | 0
c) | 4 x 24 W Flame proof street light Ex-d type fixture with T5 lamps, control gear in cast alluminium alloy LM6 enclosure and toughened glass cover with all accessories. The enclosure shall be of IP: 65 suitable for Zone 1& 2 gas group IIA & IIB . Similar to CGL model FSL 424 . | Set | 16 | 48 |  | 0
d) | Surface mounted LED type lighting fixture including 36 W LED Lamp,driver and other accessories Similar to CGL cat.No. LCTLR-36-CDL. | Set | 9 | 27 |  | 0
e) | Surface mounted Industrial vapour proof IP65 luminaire including 39 W LED,driver ,with polycarbonate housing and other accessories similar to Wipro model LE20-491-XXX-67-XX. | Set | 1 | 3 |  | 0
f) | Energy saving surface mounted 6 W LED decorative Luminaire with LED lamp, driver,thermally conductive housing and PMMA diffuser.Similar to CG Catl No. LCSR-06-CDL. | Set | 3 | 9 |  | 0
g) | 7 W LED Light fitting,Linear mirror light provided with high output PMMA diffuser, LED lamp ,driver and other accessories .Similar to CG cat. No. LCL-07-CDL. | Set | 1 | 3 |  | 0
2 | Supply of the underlight for the canopy as specified including FLP lighting fixture, 72W LED lamp , driver ,similar to Baliga Cat.No. ECRF-236, FLP juction box etc. as required. | No. | 6 | 18 |  | 0
3 | 1200mm sweep Ceiling fan including suitable down rod.Energy star rating for the equipment shall be considered 5 star rated. | Nos. | 1 | 3 |  | 0
4 | 380mm Sweep Exhaust fan, single phase propeller type having bird screen mesh /louvers complete with mounting bracket, rubber pads of suitable thickness to absorb vibrations, etc.Energy star rating for the equipemnt shall be considered as 5 star rated. | Nos. | 2 | 6 |  | 0
5 | 380mm Sweep FLP Exhaust fan, single phase propeller type having bird screen mesh /louvers complete with mounting bracket, rubber pads of suitable thickness to absorb vibrations, etc.Energy star rating for the equipemnt shall be considered as 5 star rated. | Nos. | 1 | 3 |  | 0
6 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing modular socket along with modular switch of required rating as specified below, connections etc. as required.outlet and
a) | 16A/6A , 5 in 1 socket outlet with safety shutter along with 16A Piano switch in modular type boxes | Nos. | 16 | 48 |  | 0
b) | 16A ,Socket outlet with safety shutter along with C Curve,16A TP MCB in modular type boxes . | Nos. | 3 | 9 |  | 0
c) | 6A , 5 in 1 socket outlet along with 6A Piano switch in modular type boxes | Nos. | 15 | 45 |  | 0
7 | 16A Rotary Switch in FLP LM6 Aluminium alloy , IP 65 enclosure for controlling canopy light fittings. | Nos. | 2 | 6 |  | 0
8 | Supply of Switchboards : | - | -
a) | Floor mounted PDB consiisting of Bus bar chamber, Capacitor panel, Incoming and Outgoing feeders as per Tender Drg.No.MEC/23RT/01/E1/D2/CN/ST/0413 & tender specification. | No. | 1 | 3 |  | 0
b) | Floor mounted Emergency panel consisting of bus bar chamber, cable alley, incoming & outgoing MCCB feeders as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0414 & as per tender specification. | No. | 1 | 3 |  | 0
c) | Wall/Column mounted LDB-1 (For Building Lighting Points) as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0415 & as per tender specification. | No. | 1 | 3 |  | 0
d) | Wall/Column mounted LDB-2 (For Building Power Points) as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0416 & as per tender specification | No. | 1 | 3 |  | 0
e) | Wall/Column LDB-3 (For Outdoor Lighting) consisting of PB, indication Lamp etc. as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0417 & as per tender specification | No. | 1 | 3 |  | 0
f) | LT Distribution box (2 mm thk. SMC sheet) 160 AMPS ,TPN,MCCB 415 V, 50kA for 1 sec., IP 55, cable entry side and bottom as per tender specification along with mounting arrangement and other accessories-BESCOM APPROVED MAKE. | No. | 1 | 3 |  | 0
9 | Earthing pits comprising, 3.5 meter long 50 mm dia. GI pipe electrode, charcoal, salt, GI earthing conductor for interconnecting the electrodes,6mm thick CI checked plate for cover ,CI earth pit marker, erection accessories confirming to IS- 3043 and as per technical specification.It shall also include brick masonry chamber and all other civil works | Nos. | 12 | 36 |  | 0
10 | Galvanised (GI) earth conductor .
a) | GI Strip (50X6) mm | Mtr. | 200 | 600 |  | 0
b) | GI Strip (25X3) mm | Mtr. | 350 | 1050 |  | 0
c) | 8 SWG GI wire | Mtr | 100 | 300 |  | 0
d) | 16 sq.mm braided copper wire | Mtr | 5 | 15 |  | 0
11 | Crocodile Clamp of Brass | No. | 1 | 3 |  | 0
12 | Supply of 1.1kV grade XLPE insulated, PVC sheathed ST2 , FRLS armoured Cables (conforming to IS:7098 and specification) of following sizes: | - | -
a) | 3.5 x 95 mm2 A2XFY | Mtr. | 100 | 300 |  | 0
b) | 3.5 X 50 mm² A2XFY | Mtr. | 20 | 60 |  | 0
c) | 3.5 X 25 mm² A2XFY | Mtr. | 20 | 60 |  | 0
d) | 4x16 mm² A2XFY | Mtr | 50 | 150 |  | 0
e) | 4x10 mm² 2XWY | Mtr. | 50 | 150 |  | 0
f) | 4x6 mm² 2XWY | Mtr | 50 | 150 |  | 0
g) | 4x2.5 mm² 2XWY | Mtr. | 1150 | 3450 |  | 0
h) | 2x2.5 mm² 2XWY | Mtr. | 250 | 750 |  | 0
13 | Supply of 1.1 Kv grade cable FLP,double compression type Brass cable glands as per Tender Specification for the following sizes of cables:
a) | 3.5 x 95 mm2 A2XFY | Nos. | 2 | 6 |  | 0
b) | 3.5 X 50 mm² A2XFY | Nos. | 2 | 6 |  | 0
c) | 3.5 X 25 mm² A2XFY | Nos. | 4 | 12 |  | 0
d) | 4x16 mm² A2XFY | Nos. | 4 | 12 |  | 0
e) | 4x10 mm² 2XWY | Nos. | 2 | 6 |  | 0
f) | 4x6 mm² 2XWY | Nos. | 2 | 6 |  | 0
g) | 4x2.5 mm² 2XWY | Nos. | 52 | 156 |  | 0
h) | 2x2.5 mm² 2XWY | Nos. | 4 | 12 |  | 0
14 | Supply of 1.1 Kv grade cable with heavy duty crimping type Copper lugs etc as per Tender Speciifcation for the following sizes of cables:
a) | 3.5 x 95 mm2 A2XFY | Nos. | 8 | 24 |  | 0
b) | 3.5 X 50 mm² A2XFY | Nos. | 8 | 24 |  | 0
c) | 3.5 X 25 mm² A2XFY | Nos. | 16 | 48 |  | 0
d) | 4x16 mm² A2XFY | Nos. | 16 | 48 |  | 0
e) | 4x10 mm² 2XWY | Nos. | 8 | 24 |  | 0
f) | 4x6 mm² 2XWY | Nos. | 8 | 24 |  | 0
g) | 4x2.5 mm² 2XWY | Nos. | 208 | 624 |  | 0
h) | 2x2.5 mm² 2XWY | Nos. | 8 | 24 |  | 0
15 | Supply of 3CX 95 sq.mm, 11kV(E) grade XLPE insulated, PVC sheathed ST2 ,Semi conductor screen , aluminium conductor , armoured Cables (conforming to IS:7098 and specification). | Mtr. | 25 | 75 |  | 0
16 | Indoor Cable end termination kits suitable for 11 kV, 3x95 sq.mm XLPE cable (Heat shrinkable type). | Set | 2 | 6 |  | 0
17 | Supply and Wiring with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class 25mm PVC conduit alongwith 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | No. | 31 | 93 |  | 0
18 | Point wiring for primary & secondary points of light/Fans point/ exhaust fan point/ socket point with FRLS PVC insulated copper conductor single core cable of size indicated below in surface / recessed medium class 19 mm PVC conduit,with piano type switch, phenolic laminated sheet, suitable size G.I. box and earthing the point with FRLS PVC insulated copper conductor single core cable of size indicated below etc. as required.The scope also covers supply and laying of PVC conduit, the pulling of wire from switchbox to lighting/fan point through the conduit and connecting both the ends with all accessories, like switch box, junction boxes & couples, pull boxes etc including breaking of walls /floors, earthing etc.)
a) Primary point (For Lighting point)
| Supply & wiring of light point including 1 no. 6 Amp 240 V snap on grid system modular type switch with mounted front plate to match with the interior made with shielded contact (polycarbonate) and along with recess mounting G.I box of adequate size with two no. of 2.5 sq.mm + one (earth green ) runs of 1.5 sq.mm wire etc. as indicated in Sl. No. 14. | Nos. | 12 | 36 |  | 0
b) Secondary points ( For lighting upto 3 points in a group)
| Supply and wiring of subsequent light points controlled by primary points described as above, with two no. of 2.5 sq.mm + one (earth-green) runs of 1.5 sq.mm wire etc as indicated in Sl. No. 18. | Nos. | 10 | 30 |  | 0
c) Ceiling fan & Exhaust fan points
| Supply and wiring for ceiling/ wall mounted fan point / exhaust fan point with 1 no. 10Amp 240V modular switch and electronic regulator (only for ceiling fans) mounted snap on grid system type front plate to match with the interior made with shielded contact (polycarbonate) and along with recess mounting G.I box of adequate size with two + one (earth green ) runs of 2.5 sq.mm as indicated in Sl. No. 18. | Nos. | 3 | 9 |  | 0
d) Primary Point (For 6A Socket Outlet with Switch)
| Supply and wiring of socket outlet with switch with two no. of 2.5 sq.mm + one (earth-green) runs of 1.5 sq.mm wire etc as indicated in Sl. No. 18. | Nos. | 5 | 15 |  | 0
e) Primary Point (For 6A Socket Outlet with Switch)
| Supply and wiring of susequent socket outlet with switch controlled by Primary point with two no. of 2.5 sq.mm + one (earth-green) runs of 1.5 sq.mm wire etc as indicated in Sl. No. 18. | Nos. | 5 | 15 |  | 0
19 | Supply of following sizes of class 'B' G.I.Pipe including all material and labour as per specification and drawings approved
a) | 40mm NB | Mtr. | 20 | 60 |  | 0
b) | 50 mm NB | Mtr. | 500 | 1500 |  | 0
c) | 80 mm NB | Mtr. | 300 | 900 |  | 0
d) | 100 mm NB | Mtr. | 20 | 60 |  | 0
20 | Supply of following sizes of PVC Pipe
a) | 19 mm NB | Mtr. | 20 | 60 |  | 0
b) | 25 mm NB | Mtr. | 20 | 60 |  | 0
c) | 40 mm NB | Mtr. | 20 | 60 |  | 0
d) | 60 mm NB | Mtr. | 20 | 60 |  | 0
e) | 100 mm NB | Mtr. | 20 | 60 |  | 0
21 | Supply of following including necessary clamp, bolts, rawl plugs etc. | - | -
a) | Shock hazard charts | Nos. | 1 | 3 |  | 0
b) | First Aid Boxes | Nos. | 1 | 3 |  | 0
c) | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark, Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate. | Nos. | 3 | 9 |  | 0
d) | Caution boards | Nos. | 3 | 9 |  | 0
e) | Single Line Diagram in teak wood wall cabinet with glass door | No. | 1 | 3 |  | 0
f) | Wooden key box with glass cover | No. | 1 | 3 |  | 0
22 | Supply of 1.1kV grade insulated mats required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per IS 15652 and Indian Electricity Rules. | Sq.Mtr. | 8 | 24 |  | 0
23 | Supply of latest model( 5 stars BEE certified) 1.5 T split AC complete with remote control unit, 5 KVA stablizer, MS painted Stand for outdoor unit etc. | Nos. | 1 | 3 |  | 0
24 | Supply of 63kVA ,11/0.433kV Outdoor type, 3 Ph, 50Hz, Aluminium wound,Dyn11, ONAN Distribution Transformer complete with all accessories and first oil filled. Termination arrangement for HV side & LV side and all miscellaneous civil materials required to complete HT & LT installation as indiacted in the tender speciifcation no. . | No | 1 | 3 |  | 0
25 | Supply of 150mm GI ladder type cable tray along with all accessories etc. | Mtrs | 4 | 12 |  | 0
26 | Supply of 2 Coats of Primer Painted & Fabricated support structure. | Kg | 200 | 600 |  | 0
TOTAL FOR ELECTRICAL (SUPPLY) WORKS
ELECTRICAL WORKS - ERECTION
1 | Installation, testing, commissioning of lighting fixtures complete with mounting bracket, flame proof/non flame proof fixture, glands, lugs etc. including minor civil works with pipe inserts for cables and all associated work as per specifications, drawings and instruction of Engineer-in- charge. Work to be completed in all respects. | - | -
a) | Street lighting pole 6mtr high GI octagonal pole complete with bracket, GI clamps for fixing flame proof Junction Box, and other accessories as required as per standard drawing & tender specification. | Set | 12 | 36 |  | 0
b) | FLP Junction box for terminating Loop in & Loop Out cable. | Set | 12 | 36 |  | 0
c) | 4 x 24 W Flame proof street light Ex-d type fixture with T5 lamps, control gear in cast alluminium alloy LM6 enclosure and toughened glass cover with all accessories. The enclosure shall be of IP: 65 suitable for Zone 1& 2 gas group IIA & IIB . Similar to CGL model FSL 424 . | Set | 16 | 48 |  | 0
d) | Surface mounted LED type lighting fixture including 36 W LED Lamp,driver and other accessories Similar to CGL cat.No. LCTLR-36-CDL. | Set | 9 | 27 |  | 0
e) | Surface mounted Industrial vapour proof IP65 luminaire including 39 W LED,driver ,with polycarbonate housing and other accessories similar to Wipro model LE20-491-XXX-67-XX. | Set | 1 | 3 |  | 0
f) | Energy saving surface mounted 6 W LED decorative Luminaire with LED lamp, driver,thermally conductive housing and PMMA diffuser. Similar to CG Catl No. LCSR-06-CDL. | Set | 3 | 9 |  | 0
g) | 7 W LED Light fitting,Linear mirror light provided with high output PMMA diffuser, LED lamp ,driver and other accessories .Similar to CG cat. No. LCL-07-CDL. | Set | 1 | 3 |  | 0
2 | Erection , testing and commissioning of the underlight for the canopy as specified including FLP lighting fixture, 72W LED lamp , driver ,similar to Baliga Cat.No. ECRF-236, FLP juction box etc. as required. | No. | 6 | 18 |  | 0
3 | 1200mm sweep Ceiling fan including suitable down rod.Energy star rating for the equipment shall be considered 5 star rated. | Nos. | 1 | 3 |  | 0
4 | 380mm Sweep Exhaust fan, single phase propeller type having bird screen mesh /louvers complete with mounting bracket, rubber pads of suitable thickness to absorb vibrations, etc.Energy star rating for the equipemnt shall be considered as 5 star rated. | Nos. | 2 | 6 |  | 0
5 | 380mm Sweep FLP Exhaust fan, single phase propeller type having bird screen mesh /louvers complete with mounting bracket, rubber pads of suitable thickness to absorb vibrations, etc.Energy star rating for the equipemnt shall be considered as 5 star rated. | Nos. | 1 | 3 |  | 0
6 | 16A Rotary Switch in FLP LM6 Aluminium alloy , IP 65 enclosure for controlling canopy light fittings. | Nos. | 2 | 6 |  | 0
7 | Installation, testing, commissioning of Switchboards : | - | -
a) | Floor mounted PDB consiisting of Bus bar chamber, Capacitor panel, Incoming and Outgoing feeders as per Tender Drg.No.MEC/23RT/01/E1/D2/CN/ST/0413 & tender specification. | No. | 1 | 3 |  | 0
b) | Floor mounted Emergency panel consisting of bus bar chamber, cable alley, incoming & outgoing MCCB feeders as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0414 & as per tender specification. | No. | 1 | 3 |  | 0
c) | Wall/Column mounted LDB-1 (For Building Lighting Points) as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0415 & as per tender specification. | No. | 1 | 3 |  | 0
d) | Wall/Column mounted LDB-2 (For Building Power Points) as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0416 & as per tender specification | No. | 1 | 3 |  | 0
e) | Wall/Column LDB-3 (For Outdoor Lighting) consisting of PB, indication Lamp etc. as specified in tender drg. no. MEC/23RT/01/E1/D2/CN/ST/0417 & as per tender specification | No. | 1 | 3 |  | 0
f) | LT Distribution box (2 mm thk. SMC sheet) 160 AMPS ,TPN,MCCB 415 V, 50kA for 1 sec., IP 55, cable entry side and bottom as per tender specification along with mounting arrangement and other accessories-BESCOM APPROVED MAKE. | No. | 1 | 3 |  | 0
8 | Erection , testing and commissioning of Earthing pits comprising, 3.5 meter long 50 mm dia. GI pipe electrode, charcoal, salt, GI earthing conductor for interconnecting the electrodes,6mm thick CI checked plate for cover ,CI earth pit marker, erection accessories confirming to IS- 3043 and as per technical specification.It shall also include brick masonry chamber and all other civil works | Nos. | 12 | 36 |  | 0
9 | Galvanised (GI) earth conductor .
a) | GI Strip (50X6) mm | Mtr. | 200 | 600 |  | 0
b) | GI Strip (25X3) mm | Mtr. | 350 | 1050 |  | 0
c) | 8 SWG GI wire | Mtr | 100 | 300 |  | 0
d) | 16 sq.mm braided copper wire | Mtr | 5 | 15 |  | 0
10 | Crocodile Clamp of Brass | No. | 1 | 3 |  | 0
11 | Installation, testing, commissioning of 1.1kV grade XLPE insulated, PVC sheathed ST2 , FRLS Electrical Power and Control Cables (conforming to IS:7098 and specification) of following sizes: | - | -
a) | 3.5 x 95 mm2 A2XFY | Mtr. | 100 | 300 |  | 0
b) | 3.5 X 50 mm² A2XFY | Mtr. | 20 | 60 |  | 0
c) | 3.5 X 25 mm² A2XFY | Mtr. | 20 | 60 |  | 0
d) | 4x16 mm² A2XFY | Mtr | 50 | 150 |  | 0
e) | 4x10 mm² 2XWY | Mtr. | 50 | 150 |  | 0
f) | 4x6 mm² 2XWY | Mtr | 50 | 150 |  | 0
g) | 4x2.5 mm² 2XWY | Mtr. | 1150 | 3450 |  | 0
h) | 2x2.5 mm² 2XWY | Mtr. | 250 | 750 |  | 0
12 | Installation, Commissioning of 1.1 Kv grade cable double compression type Brass cable glands as per Tender Specification for the following sizes of cables:
| 3.5 x 95 mm2 A2XFY | Nos. | 2 | 6 |  | 0
| 3.5 X 50 mm² A2XFY | Nos. | 2 | 6 |  | 0
| 3.5 X 25 mm² A2XFY | Nos. | 4 | 12 |  | 0
| 4x16 mm² A2XFY | Nos. | 4 | 12 |  | 0
| 4x10 mm² 2XWY | Nos. | 2 | 6 |  | 0
| 4x6 mm² 2XWY | Nos. | 2 | 6 |  | 0
| 4x2.5 mm² 2XWY | Nos. | 52 | 156 |  | 0
| 2x2.5 mm² 2XWY | Nos. | 4 | 12 |  | 0
13 | Installation, Commissioning of 1.1 Kv grade cable with heavy duty crimping type Copper lugs etc as per Tender Speciifcation for the following sizes of cables:
| 3.5 x 95 mm2 A2XFY | Nos. | 8 | 24 |  | 0
| 3.5 X 50 mm² A2XFY | Nos. | 8 | 24 |  | 0
| 3.5 X 25 mm² A2XFY | Nos. | 16 | 48 |  | 0
| 4x16 mm² A2XFY | Nos. | 16 | 48 |  | 0
| 4x10 mm² 2XWY | Nos. | 8 | 24 |  | 0
| 4x6 mm² 2XWY | Nos. | 8 | 24 |  | 0
| 4x2.5 mm² 2XWY | Nos. | 208 | 624 |  | 0
| 2x2.5 mm² 2XWY | Nos. | 8 | 24 |  | 0
14 | Installation , Testing and Commissioning of 3CX 95 sq.mm, 11kV(E) grade XLPE insulated, PVC sheathed ST2 ,Semi conductor screen , aluminium conductor , armoured Cables (conforming to IS:7098 and specification) | Mtr. | 25 | 75 |  | 0
15 | Installation of Indoor Cable end termination kits suitable for 11 kV, 3x95 sq.mm XLPE cable (Heat shrinkable type). | Set | 2 | 6 |  | 0
16 | Installation of following sizes of class 'B' G.I.Pipe including all associated civil work with all material and labour as per specification and drawings | - | -
a) | 40 mm NB | Mtr. | 20 | 60 |  | 0
b) | 50 mm NB | Mtr. | 500 | 1500 |  | 0
c) | 80 mm NB | Mtr. | 300 | 900 |  | 0
d) | 100 mm NB | Mtr. | 20 | 60 |  | 0
17 | Erection, Commissionng of following sizes of PVC Pipe | - | -
a) | 19 mm NB | Mtr. | 20 | 60 |  | 0
b) | 25 mm NB | Mtr. | 20 | 60 |  | 0
c) | 40 mm NB | Mtr. | 20 | 60 |  | 0
d) | 60 mm NB | Mtr. | 20 | 60 |  | 0
e) | 100 mm NB | Mtr. | 20 | 60 |  | 0
18 | Installation of following including necessary clamp, bolts, rawl plugs etc. | - | -
a) | Shock hazard charts | Nos. | 1 | 3 |  | 0
b) | First Aid Boxes | Nos. | 1 | 3 |  | 0
c) | Carbon-di-oxide(CO2) type fire extinguisher 4.5 Kg capacity Complete with gunmetal valve conforming to IS : 3224 With ISI mark, Discharge horn with bend & wall fixing Bracket With Mfg. Test certificate. | Nos. | 3 | 9 |  | 0
d) | Caution boards | Nos. | 3 | 9 |  | 0
e) | Single Line Diagram in teak wood wall cabinet with glass door | No. | 1 | 3 |  | 0
f) | Wooden key box with glass cover | No. | 1 | 3 |  | 0
19 | Installation, testing, commissioning of 1.1kV grade insulated mats required for maintenance of electrical equipment in substation as required including cutting to required shape in running length and including all labour and materials etc. complete and as per directions of Engineer-In-Charge as per IS 15652 and Indian Electricity Rules. | Sq.Mtr. | 8 | 24 |  | 0
20 | Installation of latest model( 5 stars BEE certified) 1.5 T split AC complete with remote, 5 KVA stablizer, MS Stand for outdoor unit etc. | Nos. | 1 | 3 |  | 0
21 | Installation, testing, commissioning of 63 KVA , 11 kV/433 V outdoor type,3Ph,50Hz, copper wound,Dyn11,ONAN distribution transformer complete with all accessories and first oil filled. Termination arrangement for HV side & LV side . | No | 1 | 3 |  | 0
22 | Intallation testing and commissioning of 150mm,GI Cable traysalong with all accessories, labour , civil works etc. | Mtrs | 4 | 12 |  | 0
23 | Erection,testing and commissioning of 2 Coats of Primer Painted & Fabricated support structure. | Kg | 200 | 600 |  | 0
TOTAL FOR ELECTRICAL (Erection) WORKS
TOTAL FOR ELECTRICAL (SUPPLY+ERECTION) WORKS
Note for Electrical :
Above quantities are estimated quantities and may change during detail engineering as per site condition. Contractor shall supply the equipments, at the same rate ,as per these change quantities. Payment shall be made as per quantities erected.
The cable size mentioned in SLD are indicative.The final size shall be based on the actual requirement and the size shall be selected from SOR .
Makes of all equipemnts shall be as per preferred make list.Items for which preferred makes are not indicated shall be provided only after approval of the make by owner / consultant.

## CNG INST
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3(Three) nos. of CNG mother station | Unit Rate | Total Amount for 3(Three) nos. of CNG mother stations exclusive of GST (in Rs.)
|  |  | A | B | C | D=C*B
PART III-INSTRUMENTATION WORKS
SUPPLY
1 | 5.0 KVA ,hot reduntant, 3 phase input(415V+ 10%) and single phase output (230 V+1%) industrial type UPS with battery bank ( Sealed Maiintenance Free VRLA) etc. for 4.0 hours backup for critical load installations including intercoonnecting cables, battery stand, ACDB and all other accessories, complete in all respect including commissioning spares as per technical write up, drawing & datasheet attached. | Set | 1 | 3 |  | 0
2 | Supply of complete Electronic earthing system with necessary accessories like copper stranded conductor, Cu plates, Cu strips, GI strips, Funnel with wire Mesh, GI pipe, PVC conduit, bolts,nuts, concrete chamber with CI cover, coke/charcoal, salt & sand etc., as per technical write up, drawings, etc. | Nos. | 2 | 6 |  | 0
3 | Design, Manufacture, testing, Loading at contractor’s works, Supply& Transportation, Unloading at Project site of Coriolis CNG-Series Mass flow meter (Model CNG 50 with integral local display) based on Coriolis principle of Micro motion, USA with F-series 2700 transmitter as per the technical specification and data sheet.Mass Flow Meter model shall be certified by statutory authorities W & M India for CNG applications and it is suitable for custody transfer application. | Nos. | 2 | 6 |  | 0
TOTAL FOR SUPPLY WORKS
ERECTION
1 | 5.0 KVA , hot reduntant,3 phase input(415V+ 10%) and single phase output (230 V+1%) industrial type UPS with battery bank ( Sealed Maiintenance Free VRLA) etc. for 4.0 hours backup for critical load installations including intercoonnecting cables, battery stand, ACDB and all other accessories, complete in all respect including commissioning spares as per technical write up, drawing & datasheet attached. | No. | 1 | 3 |  | 0
2 | Intallation, testing and commissioning of complete Electronic earthing system with necessary accessories like copper stranded conductor, Copper Plates, GI strips, Funnel with wire Mesh,GI pipe, PVC conduit,bolts,nuts, concrete chamber with CI cover,coke/charcoal, salt & sand etc., | No | 2 | 6 |  | 0
TOTAL FOR ERECTION WORKS
TOTAL FOR SUPPLY + ERECTION WORKS
Notes :
(i) | Above quantities are estimated quantities and may change during detail engineering as per site condition. Successful Tenderer shall supply the equipments, at the same rate, as per these change quantities. Payment shall be made as per quantities erected.
(ii) | Makes of all equipemnts shall be as per preferred make list.Items for which preferred makes are not indicated shall be provided only after approval of the make by owner / consultant.

## CNG MECH
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3 (Three) nos. of CNG mother station | Unit Rate | Total Amount for 3(Three) nos. of CNG mother stations exclusive of GST (in Rs.)
|  |  | A | B | C | D=C*B
PART - IV : Mechanical & Piping Works
| SECTION-A : SS TUBE LAYING & TESTING | - | - |  |  | -
1.0 (a) | Laying with PVC heavy duty tube clamp of Swagelok/Parker/DK-Lok/Vaishnavi Hydraulics/Vardhaman bearings/AK Industries, Pneumatic testing with Nitrogen at 280 bar and commissioning of SS tubes along with fittings, mass flow meter and valves as given below and as per Technical Specification and scope of work including handling, lifting, transportation from stores to location of CNG stations. | - | - |  |  | -
1.1 | 1”OD X 0.120” min Wall thk. SS Tube | RM | 150 | 450 |  | 0
1.2 | ¾”OD X 0.095” min Wall thk. SS Tube | RM | 500 | 1500 |  | 0
1.3 | ½”OD X 0.083” min Wall thk. SS Tube | RM | 25 | 75 |  | 0
1.0 (b) | SUPPLY OF SS TUBES as per Technical Specification (Make:Sandvik/Tubacex/Ratnamani) | - | -
1.1 | 1”OD X 0.120” min Wall thk. ,Material SS316 SS Tube | M | 150 | 450 |  | 0
1.2 | ¾”OD X 0.095” min Wall thk.,Material SS316SS Tube | M | 500 | 1500 |  | 0
1.3 | ½”OD X 0.083” min Wall thk.,Material SS316 SS Tube | M | 25 | 75 |  | 0
| Note: Quantities beyond mentioned quantities may be provided as free issue. | - | -
0
2 | Supply of SS Fittings (Make:Swagelok/Parker/SSP/Dk-lok/Hylok) | - | -
| Quick Connect Body & Stem | - | -
2.1 | End connection:½" Tube OD, for stem & ½”NPT (F) for body Material : SS316; Rated pressure : 5000 PSI @ 70°F Temperature: 0°F to 400°F | Nos. | 6 | 18 |  | 0
| Union | - | -
2.2 | Size : ¾” OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 100 | 300 |  | 0
2.3 | Size : ½" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 5 | 15 |  | 0
2.4 | Size : 1" OD, Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 30 | 90 |  | 0
| Reducing Union | - | -
2.5 | Tube OD 3/4" x Tube OD 1/2", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6 | 18 |  | 0
2.6 | Tube OD 1" x Tube OD ¾", Material : SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6 | 18 |  | 0
| Equal Tee | - | -
2.7 | Size:½” OD x ½” OD x ½” OD, Material:SS316 (Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 5 | 15 |  | 0
2.8 | Size:¾" OD x ¾" OD x ¾" OD, Material : SS316 ( Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 60 |  | 0
2.9 | Size:1" OD x 1" OD x 1" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 8 | 24 |  | 0
| Nut | - | -
2.1 | ¾ " OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 60 |  | 0
2.11 | ½" OD, Material : SS316(Rated pressure : 6000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
2.12 | 1" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
| Front Ferrule | - | -
2.13 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 60 |  | 0
2.14 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
2.15 | 1" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
| Back Ferrule | - | -
2.16 | 3/4" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 20 | 60 |  | 0
2.17 | ½" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
2.18 | 1" OD, Material : SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 10 | 30 |  | 0
| Male Connector | - | -
2.19 | Size ¼” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6 | 18 |  | 0
2.2 | Size 1/2” NPT (M) x 3/8” OD, SS316(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 6 | 18 |  | 0
2.21 | Tube Fitting, Male Connector, 3/4 in. Tube OD x 1/2 in. Male NPT(Rated pressure : 5000 PSI @ 70°F Temperature : 0°F to 400°F) | Nos. | 3 | 9 |  | 0
0
3 | Supply of SS Ball Valves of Make:Swagelok/Parker/SSP conforming to MECON’s Technical Specification No. MEC/TS/05/62/048 for SS Ball Valves of following sizes, specifications as indicated below : | - | -
0
3.1 | 2-Way Floating Normal Bore Ball Valve ¾" | Nos. | 24 | 72 |  | 0
3.2 | 2-Way Floating Normal Bore Ball Valve ½" | Nos. | 12 | 36 |  | 0
3.3 | 3-Way Trunnion Mounted, Reducer Bore Ball Valve ½" OD end Connection and ¼” NPT (F) bottom end connection | Nos. | 6 | 18 |  | 0
3.4 | 2-Way Floating Normal Bore Ball Valve ¾" with 1" expander union on both sides | Nos. | 2 | 6 |  | 0
4 | Conductive Core Thermoplastic hose (Make: SWAGELOK /PARKER SYNFLEX/ OPW) | - | -
4.1 | 3/8” ID Conductive Core Thermoplastic Hose for CNG Service with break away coupling min. 3.0m length | Nos. | 6 | 18 |  | 0
0
0
| SECTION-B : ERECTION OF MECH. EQUIPMENT | - | -
1.0 | Handling (including lifting and transportation from Client's store within city to CNG stations) and erecting in position, the following equipment either on the foundation or on roof at ~ 3 to 4 m above ground level. Contractor's scope includes supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, etc.. Scope also includes supply of all lifting tools / necessary accessories and hiring of cranes for same. | - | -
1.1 | Cascade 4500/3000 water capacity. Erection at + 3 to 4.0 M level | Nos. | 3 | 9 |  | 0
Note: | The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may increase or decrease at site at the time of actual execution and as per the discretion of Owner/ Engineer-in-charge. The unit rate shall be operated to work out the final payment due to Contractor. | - | -
| SECTION-C : SUPPLY, ERECTION & COMMISSIONING OF MISCELLANEOUS ITEM | - | -
1.0 | Supply, erection & commissioning of following miscellaneous items as per technical specification and at locations (within the stations) as directed by EIC | - | -
1.1 | Air compressor pump (Tyre Inflator) | No. | 1 | 3 |  | 0
1.2 | Fire fighting Equipments | - | -
1.2.1 | DCP -9 Kg | Nos. | 7 | 21 |  | 0
1.2.2 | DCP -75 Kg | Nos. | 2 | 6 |  | 0
1.2.3 | CO2 – 4.5 Kg | Nos. | 3 | 9 |  | 0
1.2.4 | Sand Bucket Stand with 4 Nos. Bucket | Nos. | 5 | 15 |  | 0
1.3 | Design, manufacture, assembly & supply in well packed condition at site of 30 KVA gas generator set complete with acoustic enclosure,Control panel &AMF panel including 30mtrs length of sch.80 inlet pipe,4 nos. of socket welded elbows,2 (TWO) nos. of isolation ball valve of 800# with socket welded ends and Pressure regulators suitable to reduce the incoming gas pressure from 14 to 49 kg/cm2(g) to the required generator presuure for connecting to Gen set, flanges, nut, bolts, gasket, pipe etc all required accessories and control equipment to supply continuous electrical power as per the specification. | Nos. | 1 | 3 |  | 0
1.3.1 | Installation, Testing and Commissioning of 30 KVA gas generator set complete with Control panel & AMF Panel including hook-up from existing steel pipe line (approx 30mtrs length) to Gen set, flanges, nut bolts, gasket, pipe etc all required accessories and control equipment to supply continuous electrical power as per the specification and all associated civil works. | Nos. | 1 | 3 |  | 0
| SECTION-D : STRUCTURAL WORKS & PRESSURE GUAGES | - | -
1 | Pipe Supports & Other Structures | - | -
| Supply, fabrication and erection of all types of pipe supports like clamps, saddle, guide stops, cradles, turn buckles, anchors, T-posts; stockade/ trestle and pipe bridge for overhead piping; frames for canopy, approach ladders and platforms, crossover, cable tray supports, etc. including painting as per specification labour and supervision & complete work as per drawings, specifications and instruction of Engineer-in-charge. (Bolts, nuts, washers, U-clamps etc. for supporting shall be supplied by the Contractor within the rates quoted. These items will not be measured and paid seperately). HDPE/ rubber sheet is to be provided between support & pipe wherever required., The work is to be completed in all respect as per scope of work and specification. | M.Ton. | 1 | 3 |  | 0
| Notes: | - | -
i) | The quantities indicated above are tentative estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Owner/Owner representative.
ii) | The cost of MS bolts (permanent and service(, washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants etc., as required for the work shall be deemed to be included in the quoted rates.
iii) | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accrodance with time schedule, are deemed be included in the quoted rates.
1.1 | PRESSURE GAUGES |  |  | 0
| Supply, installation and calibration of pressure Gauges and their accessories inclusive of supply of necessary piping materials/tubings alongwith all necessary valves & fittings, fabrication and installation of impulse lines/manifolds as per D. S. No. MEC/23H7/05/E5/I/001/DS-PG of WIKA / AN instruments etc. | No. | 3 | 9 |  | 0
TOTAL FOR MECHANICAL WORKS

## CNG STRL
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
Item No. | Description | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3 (Three) nos. of CNG mother station | Unit Rate | Total Amount for 3 (Three) nos. of CNG mother stations exclusive of GST (in Rs.)
PART V : STEEL STRUCTURAL WORKS
ST-1 | Structural Steel Works for Canopy & Other Allied Structures
| Supply of steel consisting of Plates, Rolled steel joists, Channels, Angles, Tubes , Rectangular / Square Hollow Steel sections, Fascia, Flashings , Rain water pipe & Gutter etc, straightening of raw steel if required . Preparation of all necessary Fabrication drawings ( Based on MECON Design drawings ) including bill of materials . Fabrication of Steel structures as per Fabrication drawings (including preparation of supplementary sketches and detailed bill of materials ) supply of bolts, nuts, washers , shims, packs, putty, gas, welding electrodes and all other consumables, as required. Cleaning and preparation of all steel surfaces by Mechanical Cleaning to St 3 of Swedish Standard for painting , Supply and application of One Coat of Primer Paint of Zinc Phosphate in Phenolic Alkyd medium 40 microns DFT , Intermediate Primer Coat of Zinc Phosphate in Phenolic Alkyd medium 40 microns DFT, One Coat of Intermediate Paint of Synthetic MIO ( ie: Micaceous Iron Oxide) 75 microns DFT , supply and application of 2 coats of Finishing paint Synthetic Enamel 25 microns DFT / coat . Finishing Coat shall be applied one Coat before erection and one coat after erection . The total thickness of paint shall be 205 Microns. Loading , Transportation and Unloading and Delivery at erection site of all fabricated structures up to height of about 12 M, erection, alignment and welding of all structures true to line, level, plumb and dimension, including rectification if any, splicing , site assembly all as per technical specifications and drawings, touch up painting, including supply of paint, where paint is damaged. | Tons | 20 | 60 |  | 0
ST-2 | Structure Steel Works for Miscellaneous Structures like Grating , Handrails , Hoardings etc
| Supplying, Fabricating & Erecting in position steel structures fabricated out of MS Girders, channels, Tees, angle, flats, plate, square hollow sections pipes etc. conforming to IS:2062 and/or from pipes conforming to IS:1161 for structural purpose for cascade supporting structure, loading/unloading platform, Gratings for platform, catladder,handrails, hoardings for sinages,Lcv stand, etc. of any size/dia for required design including cutting, welding, bolting, hoisting, fixing in position, including application of one coat of primer at shop and second coat of primer at site after erection and two coats of finishing paint at site .The work is to be completed in all respect as per specification ,scope of work, detailed construction drawings and directions of the Engineer-in-charge. | KG | 500 | 1500 |  | 0
[ Rate to include cost of all labour, nut, bolts, tools, tackles, hire charges royalties, levies, transportation, scrap value, gas cutting, welding, other consumables, paints, compressed air, water, electric power etc. all complete.]
ST-3 | Providing and fixing Fencing Gates
Supplying, fabricating & fixing fencing gates fabricated from pipes conforming to IS:1161 and plates conforming to IS:2062 & fixing of GI weldmesh made from 3mm GI wire @ 75 mm bothways to structural steel frame by means of welding/bolting, painting with enamel paint in approved shade including supply of all raw materials, bolts, electrodes, transportation etc complete as per enclosed sketch, technical specifications and directions of the Engineer-In-Charge.
a) | 4m Wide x 2.1m High | Nos. | 1 | 3 |  | 0
c) | 1m Wide x 2.1m High | Nos. | 1 | 3 |  | 0
ST- 4 | Providing and Fixing 6 O/P Chequered Plate Covers
| Providing and fixing chequered plate in approved panel or over steel structure including cutting, welding, hoisting, fixing in position, and applying two or more coats of approved quality synthetic enamel over a priming coat of approved steel primer etc complete as per scope detailed drawings , technical specifications and directions of the Engineer-In-Charge. | KG | 500 | 1500 |  | 0
[ Rate to include cost of all labour, nut, bolts, stiffening sections, bars tools, tackles, hire charges, royalties, levies, transportation, scrap value, gas cutting, welding, other consumables, paints, compressed air, water, electric power etc. all complete.]
ST-5 | Providing and fixing safety guard
| Providing and fixing safety guard with 80 mm heavy duty G.I. Pipe ( size 450 deep and 300 width inside) grouted with ready mix high strength grout mortor of approved manufacturer and painted with approved quality paint as per scope of work , detailed construction drawings, technical specifications and directions of Engineer-In-Charge. [Rate to include cost of all labour , tools , tackles etc. complete]. | Nos. | 20 | 60 |  | 0
ST- 6 | Providing and fixing Colour Coated Sheets
| Preparation of sheeting drawings, procurement, transportation and delivery at erection site of colour coated steel sheets for roof & side cladding shall be of Galvalume/zincalume BHP steel sheet made of cold rolled steel of 300 MPA minimum yield strength conforming to ASTM A366 or AS 1595. Base metal thickness shall be 0.5mm and total thickness of colour coated profiled sheet shall be 0.58mm. Fixing of sheets with all flashings, corners, ridges, cutting, bending of sheets to a required shape & size and erecting them in roof & sides with all fixing arrangement as per manufactures instructions and complete in all respect as per drawings and specifications. (Net laid area to be measured.) | Sq.Mt | 150 | 450 |  | 0
ST-7 | Providing and fixing Trac ( 150 F ) Pre-Coated False Ceiling System
| Preparation of sheeting drawings, procurement, transportation and delivery at erection site Trac ( 150 F ) Pre-Coated Steel False Ceiling System with powder coated finishes as per Manufacturers Instructions and Specifications. | Sq.Mt | 140 | 420 |  | 0
Notes:
1 | Rate to include cost of all labour, tools, tackles, equipment, hire charges, supply of all materials such as structural steel, purlins, nuts, bolts, washers, screws, seals, wire ropes,flashing,fitting and fixtures,gutter, rain water pipes and bends, electrodes, edge colour coated sheets for signage works,primer, paint and all consumables etc. with all bye works and sundry works complete in all respect.
2 | The quantities indicated are estimated values and hence are approximate. Final payment will be made based on actual quantities to be certified by the Purchaser.
3 | The cost of MS bolts (permanent and service), washers, electrodes, putty, gases, cost of straightening the raw materials, cutting of flats from plates and providing splices, paints, tools, plants, etc., as required for the work shall be deemed to be included in the quoted rates.
4 | All handling and transport charges of raw materials and fabricated structures including double handling, as required, for completion of work in accordance with Time schedule, are deemed be included in the quoted rates.
5 | All accessories like MS tower bolts, MS Pivot, MS Wheels, MS Tee section, locking arrangement etc. shall be measured by weight only.
6 | Contractor shall ensure proper alignment and smooth operation of Gate.
TOTAL FOR STRUCTURAL WORKS

## CNG ARCH
BID DOCUMENT NO.: GGPL/KKD/C&P/CW/2523/VS
CNG MOTHER STATIONS
S.NO. | Description of Item | Unit | Quantity for 1(one) no. of CNG mother station | Total Quantity for 3 (Three) nos. of CNG mother station | Unit Rate | Total Amount for 3(Three) nos. of CNG mother stations exclusive of GST (in Rs.)
|  |  | A | B | C | D=C*B
1 | Supply & installation of 4mm thick ACM of approved make alongwith required frame of MS section cladding in a combination of corporate colours in approved pattern and shade of GGPL with the use of Retro Reflective Sheeting along with all fixtures, scafolding etc complete. for CANOPY FASCIA.
1.1 | 4mm thick ACM | SQM | 60 | 180 |  | 0
1.2 | Retro Reflective sheet | SQM | 21 | 63 |  | 0
1.3 | GGPL Letters on acrylic with LED lightning inside including all cabling works | 1 set | 1 | 3 |  | 0
1.4 | LOGO on acrylic with LED lightning inside including all cabling works | Each | 1 | 3 |  | 0
2 | Supply & installation of 4mm thick ACM of approved make alongwith required frame of MS section cladding in a combination of corporate colours in approved pattern and shade of GGPL GAS with the use of Retro Reflective Sheeting along with all fixtures, scafolding etc complete. for BUILDING FASCIA.
2.1 | 4mm thick ACM | SQM | 10 | 30 |  | 0
2.2 | Retro Reflective sheet | SQM | 2 | 6 |  | 0
3 | Supply & installation of all materials for SPREADER (1200 X450X150mm thick rectangular and 100mm away from column face) including 4mm thick ACM (Aluminium Composite Material) cladding along with required MS frame etc., with the use of Retro Reflective Sheeting in required size & shape along with all fixtures, scaffolding etc., on structural framework of canopy in 10 mm thick Acrylic duly CNC Routed in require shape & Size as per direction of Engineer In Charge. | Each | 2 | 6 |  | 0
4 | Supply & installation of all materials for MANDATORY SIGNs at various facilities of CNG Station and of various sizes with 4mm thick. ACM (Aluminum Composite Material) sheets along with all fixtures . Item include Matter/Logo (as approved) in Retro Reflective Sheeting duly pasted on ACM in required size & shape. all complete as per direction of Engineer In Charge.. | Sqm | 2 | 6 |  | 0
5 | Supply & installation of DIRECTION SIGN of size 1000mm X 500mm X 250mm as per drawing standing 325 mm above finished footing level with 4mm thick. ACM (Aluminum Composite Material) of approved make / colour & Shade cladded to MS framework with the use of approved Retro Reflective Sheeting of approved make duly pasted on ACM in require size & shape duly CNC Routed as per direction of Engineer Incharge. | Each | 2 | 6 |  | 0
6 | Supply & installation of CANOPY COLUMN CLADDING over the structural column with 4mm thick ACM (Aluminum Composite Material) of approved colour with all necessary fittings and fixtures. The item includes required MS Frame if any and scaffolding and fixtures etc as per direction of Engineer Incharge. | Sqm | 40 | 120 |  | 0
7 | Supply and installation of Signage/Monolith as per enclosed drawing of monolith structure. The item is lump sum and shall includes all relevent costs associated with putting up such facility incl supply, fabrication, erection, assembly, commissioning the GGPL. MONOLITH including electrical cabling and lighting etc for the same. | Each | 1 | 3 |  | 0
7.1 | Cladding: Providing and fixing 4mm ACM to be used for cladding duly by cold forming, CNC machine routed and fold as per drawing including MS framework.
7.2 | Company Logo: On top of aluminium cladding as per drawing with Acrylic / PETG thermoformed shape & letters(as per art work) coverd with vinyl of approved make with the provisions of illuminations during night with LED of approved make with necessary electrical fittings.
7.3 | Letters: Acrylic / PETG thermoformed shape & letters(as per art work) letters of lit during night through LED lights and also having provisions of price change unit of products.
7.4 | Signs: Retro reflective vinyls pasting on front face of monolith for signages as per the artwork.
TOTAL FOR ARCHTECTURAL WORKS